QUALITY FIELD EXECUTION SYSTEM BUILD – 2

Yes. Build 2 begins here. Now we're writing the actual field reference that you could eventually open on your tablet and use alongside CRT/Hydro-Québec's official documents.

One rule applies to everything below:

The project drawings, devis, Plan Qualité, PIE/PRIE, approved procedures, professional instructions and CRT/Hydro-Québec requirements govern. This playbook tells you how to systematically find, verify, document and close the quality requirements; it does not replace them.

I'll use:

🔵 PROJECT = obtain/confirm from actual project documentation
⚪ CONTROL = strong field-quality practice
🟠 VERIFY/ESCALATE = do not independently accept/dispose without appropriate authority

BUILD 2 — ACTUAL FIELD CONTENT

1. SITEWORK & EARTHWORKS

1.1 EXISTING CONDITIONS

This workflow establishes what existed before CRT's work affected the area.

That sounds mundane, but it protects the project against disputes and prevents existing utilities/services/structures from being inadvertently damaged.

The four main subjects are:

Existing-condition survey → Existing utilities → Protection → Demolition/removal

1.1.1 REQUIREMENTS — What governs the work?

🔵 Obtain/review

Contractual/project documents

- contract drawings;

- civil drawings;

- architectural drawings where existing buildings/interfaces are involved;

- structural drawings;

- demolition drawings;

- existing-conditions drawings;

- utility drawings;

- specifications/devis;

- demolition specifications;

- civil/sitework specifications;

- temporary-work requirements;

- environmental requirements;

- owner/Hydro-Québec requirements;

- Plan Qualité;

- applicable PIE/PRIE;

- approved demolition/execution procedures;

- professional directives;

- QMT/RFI responses;

- technical changes.

Existing information

- available existing-condition surveys;

- utility records;

- previous survey information;

- geotechnical information where relevant;

- owner-supplied records;

- photographs;

- previous reports.

Determine specifically

Before work begins, you want to know:

What stays?

What gets demolished?

What gets relocated?

What must be protected?

What services must remain operational?

What condition are existing assets currently in?

What areas are restricted?

What must be temporarily supported?

What must be disconnected before demolition?

1.1.2 PLANNING

Before field work:

A. Define the work zone

Establish:

- work limits;

- demolition limits;

- access routes;

- adjacent structures;

- existing equipment;

- underground/overhead utilities;

- interfaces with operating facilities;

- protected areas.

B. Establish baseline condition

⚪ Before disturbing anything, document the existing condition where relevant.

Examples:

- existing cracks;

- damaged pavement;

- existing concrete deterioration;

- fence condition;

- utility structures;

- existing buildings;

- drainage condition;

- existing equipment;

- surrounding property where work could affect it.

This becomes baseline evidence.

C. Identify critical interfaces

Ask:

“What could our work accidentally damage or interrupt?”

Particularly:

- electrical services;

- telecommunications;

- water;

- sewer;

- drainage;

- existing Hydro-Québec infrastructure;

- adjacent structures;

- roads;

- buried infrastructure.

D. Coordinate required verification

Determine whether the project requires:

- surveyor;

- utility locator;

- professional inspection;

- owner representative;

- environmental personnel;

- demolition specialist;

- temporary works/shoring specialist.

1.1.3 DOCUMENT CONTROL

Before relying on an existing-condition drawing:

Verify revision.

Then ask:

Does this document represent verified existing conditions, or merely available historical information?

That distinction matters enormously.

An old drawing showing a pipe at Location X does not necessarily prove the pipe is still exactly at Location X.

⚪ Field rule

Drawing information + field verification = stronger confidence.

Where required, utilities should be physically located/confirmed using the project-approved process before excavation/demolition affects them.

1.1.4 MATERIAL CONTROL

Usually limited here, but protection/demolition can involve:

- temporary barriers;

- protective coverings;

- temporary supports;

- fencing;

- shoring;

- temporary drainage;

- dust-control systems;

- replacement materials;

- temporary service materials.

Verify approved materials where contractual requirements apply.

1.1.5 INSPECTION / VERIFICATION

BEFORE WORK

Verify:

☐ limits clearly identified
☐ items to remain identified
☐ items to remove identified
☐ utilities located as required
☐ existing condition documented
☐ protection installed where required
☐ required disconnects/isolation confirmed
☐ relevant technical instructions available

DURING WORK

Watch for:

- demolition beyond limits;

- damage to retained work;

- unexpected buried services;

- undocumented structures;

- unexpected materials;

- movement/damage to adjacent construction;

- water ingress;

- unauthorized modification;

- protection being removed prematurely.

🟠 Unexpected condition

If the field condition differs materially from the drawings:

Do not improvise.

Record:

location → condition → dimensions/extent → photographs → drawing/reference → potential impact

Then communicate/escalate through the project's authorized process.

1.1.6 RECORDS / OBJECTIVE EVIDENCE

Strong evidence can include:

- dated pre-work photographs;

- existing-condition survey;

- annotated site plan;

- utility location information;

- survey information;

- demolition inspection records;

- protection inspection records;

- field observations;

- professional instructions;

- QMT/RFI responses;

- photographs during/after demolition;

- deficiency/NC records where applicable.

Photograph rule

A useful photograph should answer:

What am I looking at and where is it?

A close-up of a crack without location context is weak evidence.

Use, where appropriate:

overview → intermediate view → close-up

1.1.7 NC / DEFICIENCY

Typical potential issues:

- demolition outside approved limits;

- retained item damaged;

- existing service damaged;

- required protection missing;

- work performed contrary to approved demolition procedure;

- unexpected condition ignored;

- existing service incorrectly identified;

- required temporary support absent.

🟠 Formal classification follows CRT/HQ procedures.

1.1.8 CORRECTIVE ACTION

Generic sequence:

Detect → protect/control → document → notify → obtain authorized disposition → correct → reinspect → record

Example:

Contractor damages an existing conduit.

Do not simply photograph the repaired conduit afterward.

The quality trail should establish:

what was damaged → where → when → applicable requirement → who was informed → approved disposition → repair performed → verification/testing if required → closure evidence.

1.1.9 VERIFICATION

After corrective work:

- inspect affected area;

- compare against authorized solution;

- verify testing where required;

- photograph;

- update records;

- verify surrounding work wasn't adversely affected.

1.1.10 CLOSURE

Close only when:

☐ affected work resolved
☐ required inspections completed
☐ required testing completed
☐ records complete
☐ appropriate acceptance obtained
☐ deficiency/NC status updated
☐ no outstanding related action remains

1.1.11 REPORTING / ANALYSIS

Report meaningful issues such as:

- unexpected existing conditions;

- utility conflicts;

- recurring damage;

- demolition deviations;

- impacts on subsequent work;

- unresolved technical decisions.

A recurring problem with protection may indicate a systemic quality problem, not merely isolated deficiencies.

1.1.12 QUALITY COMPLETENESS CHECK

Before declaring existing-condition work controlled:

☐ Existing conditions documented
☐ Work/removal limits understood
☐ Retained assets identified
☐ Utilities addressed
☐ Protection requirements implemented
☐ Unexpected conditions documented/escalated
☐ Demolition checked against requirements
☐ Damage documented
☐ Corrective work verified
☐ Records traceable
☐ Open issues tracked

1.2 SURVEY & LAYOUT

This is extremely important because correct workmanship in the wrong location is still wrong work.

Your QC concern isn't necessarily to perform the survey yourself. It is to verify that required survey/layout controls and records support the construction.

1.2.1 REQUIREMENTS

🔵 Obtain

- site/civil drawings;

- structural drawings;

- foundation plans;

- grading plans;

- survey drawings;

- coordinate information;

- benchmarks/datums;

- control-point information;

- specifications;

- Plan Qualité;

- applicable PIE/PRIE;

- approved survey/layout procedure where applicable;

- professional instructions;

- latest revisions.

Establish

Coordinate system?

Datum?

Reference benchmark?

Required elevations?

Building/grid axes?

Excavation limits?

Foundation coordinates?

Allowable tolerances?

🟠 Never invent tolerances from generic knowledge. Obtain the contractual/project criterion.

1.2.2 PLANNING

Before layout:

Determine what is being laid out.

For example:

Building → Grid A/1 → footing F12 → excavation limit → bottom elevation → footing elevation.

Identify:

- responsible survey personnel;

- control points;

- required verification;

- sequence;

- inspection points;

- records required;

- timing relative to excavation/formwork/concrete.

Think one operation ahead

Don't merely ask:

“Is excavation layout ready?”

Ask:

“Will today's survey information allow tomorrow's work to be correctly positioned?”

That anticipatory mindset becomes important.

1.2.3 DOCUMENT CONTROL

Verify:

☐ latest drawing
☐ latest coordinates
☐ latest dimensions
☐ latest elevations
☐ revisions reviewed
☐ technical changes incorporated
☐ conflicting information resolved

🟠 Conflict example

Civil drawing says elevation X.

Structural detail appears to imply elevation Y.

Don't choose whichever looks reasonable.

Identify conflict → document → QMT/RFI/authorized clarification → construct from resolved requirement.

1.2.4 MATERIAL CONTROL

Generally N/A except physical survey markers/protection systems.

But verify that:

- benchmarks;

- stakes;

- control points;

- reference marks

remain identifiable and protected.

A destroyed control point shouldn't casually be reconstructed from memory.

1.2.5 INSPECTION / VERIFICATION

Benchmarks

Verify as required:

- identification;

- location;

- datum/reference;

- stability;

- protection;

- evidence of disturbance.

Control Points

Check:

- point identification;

- coordinates;

- integrity;

- relationship to project control.

Building Axes

Check:

- correct grid;

- orientation;

- dimensions;

- intersections;

- offsets.

Elevations

Check relevant:

- existing grade;

- excavation bottom;

- subgrade;

- granular layers;

- footing;

- slab;

- equipment bases;

- finished elevations.

Excavation Layout

Verify:

- footprint;

- offsets;

- limits;

- depth reference;

- relationship to foundations/utilities.

Foundation Layout

Verify:

- footing/wall location;

- grid relationship;

- dimensions;

- elevations;

- anchor/embedded interfaces where applicable.

1.2.6 RECORDS / EVIDENCE

Potential records:

- survey reports;

- surveyor records;

- coordinates;

- elevation records;

- annotated drawings;

- inspection records;

- photographs of relevant controls;

- as-built survey where required;

- discrepancy records;

- approved clarifications.

The evidence should connect:

Element ID ↔ drawing/grid ↔ location ↔ elevation/coordinate ↔ date ↔ result

1.2.7 NC / DEFICIENCY

Potential issues:

- wrong grid;

- wrong elevation;

- control point disturbed;

- excavation outside layout;

- footing misplaced;

- incorrect offset;

- outdated drawing used;

- layout doesn't incorporate approved change.

Important principle

A positional error tends to propagate.

Wrong footing position can affect:

foundation → columns → steel → walls → equipment → piping → cable systems → envelope.

So dimensional/layout problems deserve early attention.

1.2.8 CORRECTIVE ACTION

If discrepancy is found:

Stop/hold affected progression where appropriate → establish actual condition → document → compare against requirement → communicate → obtain authorized disposition → correct/re-survey → reinspect.

Never assume:

“It's only 20 mm.”

Whether 20 mm matters depends on the actual requirement and interface.

1.2.9 VERIFICATION

After correction:

- re-survey;

- verify against current requirement;

- record actual coordinates/elevation;

- verify downstream interfaces;

- retain evidence.

1.2.10 CLOSURE

☐ Correct position confirmed
☐ Correct elevation confirmed
☐ Applicable tolerance satisfied
☐ Changes incorporated
☐ Required records complete
☐ Downstream construction can proceed

1.2.11 REPORTING / ANALYSIS

Track recurring:

- survey discrepancies;

- disturbed control points;

- incorrect elevations;

- revision problems;

- layout rework.

Repeated errors may indicate a process-control issue requiring attention by the Responsable qualité/site team.

1.2.12 QUALITY CHECK

☐ Correct drawing
☐ Correct datum
☐ Correct benchmark
☐ Control point valid
☐ Grid/axis correct
☐ Coordinates correct
☐ Elevation correct
☐ Tolerance verified against project requirement
☐ Discrepancies resolved
☐ Survey evidence retained
☐ Release/progression authorized where required

1.3 EXCAVATION

Now we're at the first major physical workflow.

The objective is not simply “dig the hole.”

The quality objective is:

Produce an excavation of the required geometry and elevation, without compromising adjacent work/services, and expose a bottom condition suitable for the next approved construction operation.

1.3.1 REQUIREMENTS — WHERE DO I GET THEM?

🔵 Primary project sources

Review applicable:

Drawings

- civil/site plan;

- excavation/grading plans;

- foundation drawings;

- sections;

- details;

- underground-service drawings;

- drainage drawings;

- temporary-work/shoring drawings where applicable.

Specifications

- excavation/earthworks;

- foundations;

- granular materials;

- dewatering;

- shoring;

- backfill;

- geotechnical requirements.

Quality

- Plan Qualité;

- PIE/PRIE;

- inspection forms;

- approved procedures;

- hold/witness points.

Technical

- geotechnical report;

- approved excavation procedure;

- approved shoring/temporary-work information;

- survey information;

- professional directives;

- QMT/RFI responses;

- approved technical changes.

Extract the actual acceptance criteria

Create an Excavation Requirement Sheet for the specific area:

| Item | Requirement | Source |
| --- | --- | --- |
| Excavation location | ___ | Drawing ___ |
| Limits | ___ | Drawing ___ |
| Bottom elevation | ___ | Drawing/detail ___ |
| Required bearing/subgrade condition | ___ | Geotech/devis ___ |
| Dewatering requirement | ___ | Devis/procedure ___ |
| Shoring requirement | ___ | Approved design/procedure ___ |
| Unsuitable soil disposition | ___ | Geotech/devis ___ |
| Over-excavation treatment | ___ | Project requirement ___ |
| Inspection point | ___ | PIE/PRIE ___ |

This little table is exactly the kind of thing that can make you efficient.

You're converting hundreds of pages of project documentation into the acceptance criteria for today's activity.

1.3.2 PLANNING

Step 1 — Understand tomorrow's work

From schedule/look-ahead/site coordination:

- where are they excavating?

- what element is it for?

- when?

- how much?

- what follows excavation?

- when will the bottom become unavailable/covered?

Step 2 — Identify prerequisites

Before excavation:

☐ survey/layout completed
☐ utilities addressed
☐ latest drawings available
☐ excavation procedure available where required
☐ shoring requirements addressed
☐ groundwater/dewatering considered
☐ access established
☐ excavated-material handling planned
☐ inspection requirements identified
☐ geotechnical/professional inspection coordinated where required

Step 3 — Identify the QUALITY HOLD MOMENT

One of the most important points is usually after reaching excavation bottom and before covering/modifying it with the next operation, subject to the actual PIE/PRIE.

Because once they place:

- granular material;

- mud slab;

- footing preparation;

- drainage;

- concrete;

your original bottom condition may no longer be observable.

Therefore your system should flag:

⚠️ PRE-CONCEALMENT OPPORTUNITY — BOTTOM OF EXCAVATION

1.3.3 DOCUMENT CONTROL

Before inspection, verify:

DRAWINGS

☐ correct area
☐ correct foundation/detail
☐ current revision
☐ excavation limits understood
☐ required elevation identified

TECHNICAL INFORMATION

☐ current geotechnical information
☐ current procedure
☐ applicable technical directives
☐ latest RFI/QMT answers
☐ latest change incorporated

QUALITY

☐ correct PIE/PRIE
☐ required inspection point identified
☐ correct form/checklist available

1.3.4 MATERIAL CONTROL

Excavation itself may involve limited permanent materials, but materials quickly become relevant for:

- granular replacement;

- stabilization;

- geotextile;

- drainage stone;

- lean concrete/mud slab;

- approved fill;

- temporary stabilization.

If unsuitable soil or over-excavation requires replacement material:

do not assume any available stone/fill is acceptable.

Verify:

material → approval → source → required properties → delivery → placement → testing

against project requirements.

1.3.5 INSPECTION & TESTING

This is the field core.

A. BEFORE EXCAVATION

1. Location

Verify:

- excavation area;

- grid/coordinates;

- limits;

- relationship to foundation.

2. Existing conditions

Observe:

- existing grade;

- adjacent structures;

- utilities;

- existing drainage;

- visible groundwater/wet conditions;

- access.

3. Protection

Verify relevant:

- retained infrastructure protected;

- utilities addressed;

- adjacent work protected;

- temporary works established.

B. DURING EXCAVATION

1. Excavation Limits

Compare actual excavation against required footprint.

Look for:

- excessive lateral excavation;

- insufficient width;

- encroachment;

- interference with adjacent foundations/services.

2. Depth / Elevation

Monitor progression toward required elevation.

Avoid unnecessary over-excavation.

🟠 Important

If they excavate below required elevation:

do not simply refill the hole with whatever soil is available.

The project/geotechnical requirements should determine the authorized remediation.

3. Slopes / Shoring Interfaces

Quality concern:

- excavation configuration consistent with approved arrangement;

- shoring located/configured appropriately;

- construction doesn't compromise permanent work;

- unexpected movement/damage documented.

Safety caveat: excavation stability and worker protection are also major safety matters and must follow the project's safety program and competent-person requirements. Your QC playbook should not substitute for those responsibilities.

4. Excavated Material

Observe whether material is:

- expected;

- unexpected;

- potentially unsuitable;

- contaminated/suspect where relevant;

- being segregated where required;

- being reused only where permitted.

5. Groundwater

Look for:

- water entering excavation;

- ponding;

- pumping;

- erosion;

- softening;

- soil disturbance;

- loss of fines;

- instability;

- effects on bottom condition.

Water isn't merely an inconvenience.

It can materially affect the quality of the bearing/subgrade surface.

C. BOTTOM-OF-EXCAVATION INSPECTION

This should be treated as a distinct inspection.

1. Location

Correct footprint?

2. Elevation

Correct bottom elevation?

Use appropriate survey evidence/measurement.

3. Geometry

Correct dimensions/configuration?

4. Bottom condition

Look for:

- disturbed soil;

- loose material;

- soft spots;

- organic material;

- mud;

- standing water;

- frozen material;

- unexpected rock;

- unsuitable material;

- variability;

- evidence of over-excavation.

🟠 Critical boundary

You observe and document.

You should not independently declare geotechnical bearing capacity unless you're specifically authorized and qualified to do so under the project procedure.

If the project requires geotechnical/professional acceptance:

coordinate it and obtain the required record.

D. OVER-EXCAVATION

If excavation goes too deep:

Capture immediately

Where?

Grid/location.

How much?

Actual vs required elevation.

Extent?

Length × width × approximate depth as appropriate.

Condition?

Photographs.

Requirement?

Drawing/specification reference.

Then:

control → communicate → authorized disposition → corrective work → verify

Potential remedies depend entirely on project requirements/professional direction.

Don't invent one.

E. UNSUITABLE SOILS

Possible indicators:

- organic material;

- highly disturbed soil;

- soft/pumping material;

- unexpected fill;

- excessive moisture;

- debris;

- material inconsistent with anticipated geotechnical conditions.

Again:

Observation ≠ engineering disposition.

Your job is to recognize that something may be wrong, preserve the evidence and get the correct authority involved.

F. TESTING / PROFESSIONAL VERIFICATION

Depending on the project, this might involve:

- survey verification;

- geotechnical inspection;

- proofing;

- density/compaction testing after remediation;

- other specified verification.

🔵 Actual Hochelaga PIE/PRIE and devis determine what is required.

1.3.6 RECORDS & OBJECTIVE EVIDENCE

For a strong excavation quality record, consider:

Identification

- date;

- location/grid;

- excavation ID/element;

- drawing/detail;

- revision;

- inspector;

- contractor/trade.

Inspection information

- required bottom elevation;

- actual verified elevation;

- excavation dimensions where relevant;

- bottom condition;

- groundwater condition;

- observed soil condition;

- shoring/interface observations where within scope;

- inspection/test status.

Evidence

- overview photographs;

- photographs showing location context;

- bottom-condition photographs;

- measurement/survey evidence;

- geotechnical record where required;

- test results;

- annotated drawing;

- corrective-action evidence.

Result

Conforming / pending verification / issue identified / controlled / released, according to the project's actual terminology.

1.3.7 NC / DEFICIENCY

Typical potential excavation issues:

Geometry

- wrong location;

- wrong limits;

- insufficient excavation;

- excessive excavation;

- wrong elevation.

Soil

- unsuitable material remaining;

- disturbed bottom;

- soft spots;

- unapproved fill;

- organic/debris material.

Water

- standing water;

- erosion;

- softened bottom;

- inadequate control affecting work quality.

Documentation/process

- work proceeds before required inspection;

- required hold point bypassed;

- outdated drawing used;

- required geotechnical acceptance absent;

- unapproved remediation performed.

1.3.8 CORRECTIVE ACTION

Let's make this practical.

Example — Soft area discovered at footing excavation

You inspect footing excavation F12.

Most of the bottom appears consistent, but one area is visibly soft and pumps under disturbance.

Wrong approach:

“Throw some stone there and continue.”

System approach:

1 — IDENTIFY

Grid/location + dimensions/extent + photos.

2 — REQUIREMENT

Check applicable geotechnical/devis/PIE requirement.

3 — CONTROL

Prevent affected area from being concealed/progressed where required.

4 — COMMUNICATE

Foreman/site coordination + Responsable qualité + appropriate technical/professional party according to CRT procedure.

5 — DISPOSITION

Authorized technical solution obtained.

For illustration only, it might involve removing unsuitable material and replacing it with specified material—but the project authority decides this, not our playbook.

6 — IMPLEMENT

Contractor executes authorized solution.

7 — VERIFY

Inspect replacement/remediation.

Required testing performed.

8 — EVIDENCE

Before photos + disposition + during/after photos + test records.

9 — CLOSE

Only after acceptance requirements are satisfied.

That's the complete quality loop.

1.3.9 VERIFICATION

After corrective work ask:

Was the right area corrected?

Was the authorized method followed?

Was the correct material used?

Were required lifts/placement controls followed?

Was required testing performed?

Did it pass?

Do I have evidence?

Has the technical/professional requirement been satisfied?

1.3.10 CLOSURE

Before allowing yourself to mentally mark excavation DONE:

☐ Correct limits
☐ Correct location
☐ Correct elevation
☐ Bottom condition accepted as required
☐ Groundwater issues controlled
☐ Unsuitable material addressed
☐ Over-excavation addressed
☐ Required professional/geotechnical acceptance obtained
☐ Required testing complete
☐ Open deficiencies addressed
☐ NCs properly tracked
☐ Corrective work verified
☐ Inspection record complete
☐ Photographs/evidence filed
☐ Required communication complete
☐ Next operation authorized to proceed according to project procedure

1.3.11 REPORTING / ANALYSIS

Your report shouldn't merely say:

“Excavation inspected.”

Useful quality information might look conceptually like:

Footing F12 – Grid B/4: excavation reached required geometry/elevation; localized soft area identified at southeast portion; affected work held pending technical disposition; remediation subsequently completed and verification recorded under [reference].

That tells the Responsable qualité:

where → what → status → action → reference.

Over multiple excavations, look for trends:

- repeated over-excavation;

- recurring soft areas;

- groundwater problems;

- repeated survey errors;

- frequent failed remediation tests;

- recurring bypass of inspection points.

Then the question changes from:

“Did we fix F12?”

to:

“Why have five of the last eight footing excavations experienced the same problem?”

That's quality management rather than simply inspection.

1.3.12 EXCAVATION — FIELD QUALITY CHECKPOINT

This is the quick-reference screen you'd actually want on site.

BEFORE

☐ Latest drawings/revision
☐ Devis reviewed
☐ PIE/PRIE reviewed
☐ Geotechnical requirements identified
☐ Layout verified
☐ Utilities addressed
☐ Excavation limits identified
☐ Required elevation identified
☐ Shoring/interface requirements addressed
☐ Dewatering considered
☐ Hold/witness points identified
☐ Required professional/testing personnel coordinated

DURING

☐ Excavation within limits
☐ Depth monitored
☐ Over-excavation avoided/controlled
☐ Adjacent assets protected
☐ Excavated material observed
☐ Unexpected conditions documented
☐ Groundwater controlled
☐ Bottom protected from unnecessary disturbance

BOTTOM / PRE-CONCEALMENT

☐ Correct location
☐ Correct dimensions
☐ Correct elevation
☐ Loose material removed as required
☐ No unacceptable standing water
☐ Soft/unsuitable areas addressed
☐ Over-excavation addressed
☐ Required geotechnical/professional inspection completed
☐ Required survey completed
☐ Required tests passed
☐ Photographs taken
☐ Inspection record completed

BEFORE NEXT ACTIVITY

☐ Deviations resolved/controlled
☐ Corrective work verified
☐ Required acceptance/release obtained
☐ Evidence filed
☐ Tracker updated
☐ Responsable qualité informed as required
☐ Area ready for next approved operation

Practical example — Your first excavation inspection

Imagine you arrive and the superintendent tells you:

“We're finishing excavation for foundations F10–F14 this morning and granular starts after lunch.”

Your system immediately tells you something important:

Granular will conceal the excavation bottom.

So your priority becomes:

1. Find the requirements

Foundation drawing → civil drawing → excavation specification → geotechnical requirements → PIE/PRIE → applicable technical changes.

2. Establish the criteria

For each footing:

location + dimensions + bottom elevation + bottom acceptance requirement + required inspection/test.

3. Coordinate

When will F10–F14 be ready?

Does the PIE require a specific witness/hold point?

Does geotechnical/professional personnel need to inspect?

When is granular arriving?

Now you're managing the inspection before it becomes urgent.

4. Inspect systematically

F10 → F11 → F12 → F13 → F14

Don't randomly walk around taking photographs.

For every footing:

ID → location → elevation → dimensions → bottom condition → water → abnormal conditions → evidence → status.

5. Problem at F12

Soft area.

Don't panic and don't become an amateur geotechnical engineer.

Document → identify requirement → communicate → control → authorized disposition → correction → verify.

Meanwhile F10, F11, F13 and F14 don't disappear from your system merely because F12 became interesting.

Their records still need completion.

6. Close

At the end, you should be able to account for all five:

| Excavation | Inspection | Evidence | Issue | Required verification | Status |
| --- | --- | --- | --- | --- | --- |
| F10 | ✓ | ✓ | None | Complete | Ready |
| F11 | ✓ | ✓ | None | Complete | Ready |
| F12 | ✓ | ✓ | Soft area | Pending/corrected as applicable | Hold/Open |
| F13 | ✓ | ✓ | None | Complete | Ready |
| F14 | ✓ | ✓ | None | Complete | Ready |

Now you're controlling quality rather than chasing construction.

And that distinction is going to run through this entire system:

Bad QC is reactive: construction happens → inspector discovers what happened.

Strong QC is anticipatory: understand upcoming construction → identify requirements → coordinate inspection → observe critical stages → collect evidence → control deviations → verify → close.

That is the behaviour we want this entire field system to reinforce.

Perfect. We continue with the same operating structure and the same rule:

CRT/Hydro-Québec project documents govern.
This playbook is your execution guide to make sure you identify the right requirements, plan correctly, inspect systematically, capture objective evidence, control deviations, and close the quality loop thoroughly.

1.4 SUBGRADE

The quality objective is:

Produce a stable, properly located and properly elevated formation surface that is acceptable for the next construction layer or foundation element.

Subgrade is one of those stages where poor work may not become obvious until much later. If it is weak, wet, disturbed, too high, too low, or improperly remediated, every layer above it inherits the problem.

1.4.1 REQUIREMENTS — WHERE DO I GET THEM?

🔵 PROJECT SOURCES

Review:

- civil drawings;

- grading plans;

- foundation drawings;

- sections/details;

- geotechnical report;

- earthworks specifications;

- granular/base specifications;

- foundation specifications;

- approved excavation procedures;

- Plan Qualité;

- applicable PIE/PRIE;

- survey/layout information;

- technical directives;

- QMT/RFI responses;

- approved remediation procedures where applicable.

Extract specifically

For the area being inspected:

- required subgrade elevation;

- required geometry/limits;

- required soil/material condition;

- required proofing/testing;

- moisture limitations if specified;

- bearing/acceptability criteria;

- treatment of unsuitable material;

- treatment of disturbed material;

- over-excavation/remediation requirements;

- requirement for geotechnical/professional acceptance;

- hold/witness points.

⚠️ Important

Do not independently invent a bearing-capacity criterion.

Your job is to verify the project requirement and ensure the appropriate authorized person/test confirms acceptability where required.

1.4.2 PLANNING

Before inspection, establish:

What happens next?

Is the subgrade going to receive:

- footing;

- slab-on-grade;

- granular fill;

- road base;

- drainage;

- mud slab;

- foundation preparation?

That determines how critical the inspection timing is.

Identify the inspection window

Subgrade is highly vulnerable to:

- rain;

- groundwater;

- traffic;

- freezing;

- rutting;

- overworking.

So the ideal sequence is usually:

finish excavation → prepare subgrade → inspect/test → release → place next layer

rather than:

finish excavation → leave exposed for two days → drive equipment over it → inspect after deterioration.

Coordinate

Determine whether you need:

- surveyor;

- geotechnical personnel;

- testing laboratory;

- superintendent/foreman;

- Responsable qualité;

- owner/professional representative.

1.4.3 DOCUMENT CONTROL

Verify:

☐ latest civil/foundation drawings
☐ correct required elevation
☐ current geotechnical recommendations
☐ latest technical changes
☐ applicable PIE/PRIE
☐ correct inspection form
☐ current remediation requirements

Example

If a revised foundation elevation changes from 100.250 to 100.100, then:

subgrade elevation may change too.

A technically perfect subgrade at the superseded elevation is still wrong.

1.4.4 MATERIAL CONTROL

Often the subgrade is existing soil, but materials may be introduced for:

- remediation;

- stabilization;

- levelling;

- replacement;

- separation.

If replacement material is required, verify:

- approved material type;

- approved source where applicable;

- gradation/classification requirements;

- moisture condition;

- delivery identification;

- traceability;

- storage/segregation if relevant.

1.4.5 INSPECTION / TESTING

A. CONDITION

Observe:

- loose material;

- mud;

- standing water;

- soft spots;

- pumping;

- rutting;

- frozen material;

- organic matter;

- debris;

- disturbed soil;

- unexpected fill;

- segregation;

- erosion.

Practical field question

If I place the next layer on this surface right now, am I trapping a known problem underneath?

That is the quality mindset.

B. ELEVATION

Verify:

- design elevation;

- actual elevation;

- variation across area;

- local depressions/high points.

Use survey evidence where required.

Watch for

- high subgrade reducing required granular thickness;

- low subgrade creating unapproved fill depth;

- uneven surfaces affecting subsequent layer thickness.

C. BEARING / ACCEPTABILITY

Depending on project requirements, acceptability may be established by:

- geotechnical visual assessment;

- proof rolling;

- field testing;

- prescribed inspection;

- professional sign-off.

🟠 If the condition looks suspicious but no test has yet been performed, do not simply accept it because the surface “looks okay.”

D. PROOFING / TESTING

Where required, monitor:

- area tested;

- method used;

- equipment;

- observed movement/rutting/pumping;

- failed zones;

- reworked zones;

- retest results.

Again, actual test method and acceptance criteria come from the project.

E. REMEDIATION

Potential remediation could include, depending on authorized direction:

- removal of unsuitable material;

- drying/aeration;

- compaction;

- replacement granular;

- stabilization;

- geotextile/separation;

- drainage correction.

But:

Remediation method must come from approved project requirements or authorized disposition.

1.4.6 RECORDS / OBJECTIVE EVIDENCE

Capture:

- area/grid;

- required elevation;

- actual elevation;

- date/time;

- weather/site conditions;

- bottom/subgrade condition;

- test/proofing status;

- test results;

- geotechnical/professional record;

- photographs;

- remediation locations;

- before/after evidence;

- annotated drawing;

- final acceptance status.

Good evidence should let another person identify:

where the soft area was → what was done → what test confirmed acceptability → when it was closed.

1.4.7 NC / DEFICIENCY

Potential issues:

- wrong elevation;

- soft/pumping soil;

- disturbed surface;

- standing water;

- frozen subgrade;

- unsuitable material;

- unapproved remediation;

- next layer placed before required acceptance;

- required testing skipped;

- failed area not re-tested.

1.4.8 CORRECTIVE ACTION — EXAMPLE

Scenario

During pre-granular inspection, a 2 m × 3 m area pumps visibly under equipment.

Process

1. Identify
Grid/location + approximate dimensions + photographs.

2. Requirement
Check geotechnical/devis/PIE requirements.

3. Control
Prevent granular placement over affected zone if required.

4. Communicate
Foreman/site team + Responsable qualité + required technical/geotechnical authority.

5. Obtain disposition
Approved remediation issued.

6. Execute
Contractor performs remediation.

7. Verify
Inspect and retest as required.

8. Evidence
Before/after photos + test records + disposition reference.

9. Close
Only after required acceptance.

1.4.9 VERIFICATION

Confirm:

☐ correct area remediated
☐ approved method used
☐ correct material used
☐ final elevation correct
☐ required testing complete
☐ result acceptable
☐ no remaining soft areas
☐ evidence complete

1.4.10 CLOSURE

Subgrade is ready only when:

☐ geometry correct
☐ elevation correct
☐ surface condition acceptable
☐ unsuitable areas addressed
☐ water/frost problems addressed
☐ required testing passed
☐ professional/geotechnical acceptance obtained where required
☐ records complete
☐ next activity released as required

1.4.11 REPORTING / ANALYSIS

Track recurring issues:

- soft zones;

- excessive moisture;

- repeated failed proofing;

- recurring over-excavation;

- poor drainage;

- recurring low/high elevations.

These may point to broader excavation, dewatering, survey, or traffic-control problems.

1.4.12 SUBGRADE QUALITY CHECKPOINT

BEFORE

☐ Latest drawings
☐ Geotechnical requirements
☐ Required elevation
☐ PIE/PRIE
☐ Testing/proofing requirements
☐ Remediation process understood

INSPECTION

☐ Surface stable
☐ No unacceptable water
☐ No loose/disturbed material
☐ No organic/debris material
☐ No unacceptable frozen material
☐ Elevation correct
☐ Required proofing/testing completed

BEFORE COVERING

☐ Failed zones remediated
☐ Retests acceptable
☐ Acceptance documented
☐ Photos/evidence complete
☐ Release obtained where required

1.5 GRANULAR MATERIALS

The quality objective is:

Place the correct approved granular material, in controlled lifts, at appropriate moisture, compact it to the specified requirement, and achieve the required final geometry/elevation.

This workflow applies to:

- under-slab granular;

- road base/subbase;

- foundation preparation;

- trench bedding;

- backfill layers;

- equipment pads;

- exterior works.

1.5.1 REQUIREMENTS

🔵 Obtain

- civil drawings;

- grading drawings;

- foundation/slab details;

- road/site details;

- granular material specifications;

- geotechnical report;

- approved material data;

- source approvals;

- Plan Qualité;

- PIE/PRIE;

- laboratory/test requirements;

- approved procedures;

- technical changes;

- QMT/RFI responses.

Extract

For each granular layer:

- material type/class;

- source;

- gradation/properties;

- required thickness;

- maximum lift thickness;

- moisture requirement;

- required compaction percentage;

- test method;

- test frequency;

- final elevation;

- slope;

- tolerance;

- geotextile/separation requirement;

- hold/witness points.

1.5.2 PLANNING

Before placement:

Determine the layer sequence

Example:

subgrade → geotextile → 300 mm granular A → 150 mm granular B → slab

You need to know:

- what is below;

- what comes next;

- which layer is being placed today;

- what inspection/testing must occur before the next layer.

Coordinate

- material delivery;

- source approval;

- laboratory testing;

- survey;

- compaction equipment;

- moisture conditioning;

- inspection timing.

Think in lifts

Do not treat 600 mm of granular as one inspection.

If the approved process requires 200 mm lifts:

Lift 1 → inspect/test → Lift 2 → inspect/test → Lift 3 → inspect/test

Otherwise you may lose the ability to verify the lower layers.

1.5.3 DOCUMENT CONTROL

Verify:

☐ correct detail
☐ correct layer thickness
☐ correct material designation
☐ current material approval
☐ current source approval
☐ current testing requirement
☐ latest changes incorporated

1.5.4 MATERIAL CONTROL

This is critical.

Before delivery

Verify:

- material approved;

- source approved;

- required certificates/test data available;

- correct material designation.

On delivery

Observe:

- delivery identification;

- contamination;

- segregation;

- excessive moisture/dryness;

- visible foreign material;

- consistency with approved material.

Storage

Where stockpiled:

- avoid contamination;

- avoid mixing different materials;

- maintain drainage;

- preserve identification/traceability where required.

1.5.5 INSPECTION / TESTING

A. UNDERLYING SURFACE

Before placement:

☐ previous layer/subgrade accepted
☐ correct elevation
☐ no standing water
☐ unsuitable areas resolved
☐ geotextile installed if required
☐ surface not excessively disturbed

B. PLACEMENT

Observe:

- even distribution;

- segregation;

- correct area;

- lift thickness;

- edge control;

- contamination;

- placement around structures/services.

Lift thickness

This matters because excessive lift thickness can prevent adequate compaction through the full depth.

C. MOISTURE

Observe/test as required:

- too dry;

- too wet;

- water added;

- drying performed;

- uniformity.

Actual acceptable moisture range comes from the applicable requirement.

D. COMPACTION

Observe:

- proper equipment;

- full area covered;

- edges/corners addressed;

- areas around utilities/structures compacted properly;

- no obvious rutting/pumping;

- layer remains stable.

E. DENSITY TESTING

Where specified:

Track:

- location;

- elevation/lift;

- test number;

- required density;

- actual result;

- pass/fail;

- retest after correction.

Important

One passing density test does not automatically prove the entire project is compliant.

Follow the actual testing frequency/location requirements.

F. FINAL ELEVATION / SLOPE

Verify:

- thickness achieved;

- elevation;

- slope;

- surface uniformity;

- localized depressions/high areas.

1.5.6 RECORDS / EVIDENCE

Maintain:

- material approval;

- source information;

- delivery records where required;

- layer/lift identification;

- test locations;

- density results;

- moisture results;

- photographs;

- survey/elevation records;

- annotated plan;

- failed-test records;

- corrective/retest evidence.

A strong granular record should tell you:

which material → which source → which area → which lift → which tests → which results.

1.5.7 NC / DEFICIENCY

Typical issues:

- wrong material;

- unapproved source;

- contaminated material;

- excessive lift thickness;

- insufficient compaction;

- failed density;

- wrong moisture condition;

- wrong elevation;

- wrong slope;

- next lift placed over failed/unaccepted layer;

- damaged geotextile;

- segregation.

1.5.8 CORRECTIVE ACTION — EXAMPLE

Scenario

Density test on Lift 2 fails.

Wrong approach:

“Roll it a bit more and continue.”

Better workflow:

1. Identify exact test location/lift.

2. Confirm requirement and result.

3. Control affected area.

4. Notify relevant field/quality personnel.

5. Rework according to approved method
e.g. moisture adjustment/recompaction, depending on requirement.

6. Retest.

7. Record original failure + corrective action + retest result.

8. Release next lift only when acceptable.

1.5.9 VERIFICATION

Confirm:

- failed location reworked;

- correct method used;

- retest performed;

- result passes;

- final thickness/elevation remains correct;

- evidence complete.

1.5.10 CLOSURE

Granular work complete when:

☐ approved material used
☐ source traceable
☐ all lifts within required thickness
☐ moisture controlled
☐ density tests complete
☐ failed tests resolved
☐ final elevation correct
☐ final slope correct
☐ required records complete
☐ next work released

1.5.11 REPORTING / ANALYSIS

Useful trends:

- repeated density failures;

- one supplier causing material problems;

- over-thick lifts;

- recurring wet material;

- certain equipment/operator consistently failing;

- recurring low/high elevations.

This can help the Responsable qualité act before the same issue repeats.

1.5.12 GRANULAR QUALITY CHECKPOINT

BEFORE

☐ Material approved
☐ Source approved
☐ Underlying surface accepted
☐ Layer sequence understood
☐ Lift thickness requirement known
☐ Compaction criterion known
☐ Test frequency known

DURING

☐ Correct material
☐ No contamination
☐ Lift thickness controlled
☐ Moisture appropriate
☐ Compaction complete
☐ Testing performed
☐ Failures controlled

FINAL

☐ All tests acceptable
☐ Final thickness correct
☐ Elevation correct
☐ Slope correct
☐ Records complete
☐ Area released

1.6 BACKFILL

The quality objective is:

Backfill with approved material, placed and compacted in controlled lifts, without damaging adjacent permanent construction or buried services.

Backfill differs from generic granular placement because of the interfaces.

The fill can be perfectly compacted and still be unacceptable if it damages:

- waterproofing;

- insulation;

- foundation drains;

- piping;

- conduits;

- walls;

- buried equipment.

1.6.1 REQUIREMENTS

🔵 Obtain

- civil drawings;

- foundation details;

- service/trench drawings;

- drainage drawings;

- waterproofing details;

- earthworks/backfill specifications;

- approved material requirements;

- geotechnical report;

- Plan Qualité;

- PIE/PRIE;

- procedures;

- testing requirements;

- technical changes;

- approved protection details.

Establish

- approved backfill material;

- zones requiring special material;

- maximum lift thickness;

- compaction requirement;

- testing frequency;

- required protection;

- minimum curing/strength before backfilling where applicable;

- required drainage layers;

- allowable equipment near structures;

- sequencing;

- final elevation/slope.

1.6.2 PLANNING

Before backfill:

Ask what is about to become hidden

This is a major pre-concealment stage.

Before covering, verify applicable:

- foundation wall;

- waterproofing;

- insulation;

- drainage;

- buried piping;

- conduit;

- penetrations;

- repairs;

- survey/as-built information.

If those items need documentation, get it before backfill.

Coordinate

- inspection of concealed work;

- survey/as-built;

- testing;

- material delivery;

- backfill sequence;

- access/equipment;

- protection measures.

1.6.3 DOCUMENT CONTROL

Verify:

☐ current foundation/service drawings
☐ current waterproofing/drainage details
☐ approved backfill material
☐ current technical changes
☐ applicable PIE/PRIE
☐ required pre-concealment inspection completed

1.6.4 MATERIAL CONTROL

Verify:

- material approved;

- source approved;

- free of debris/organic material;

- suitable particle size near sensitive work;

- no frozen lumps where prohibited;

- moisture suitable;

- different material zones not mixed.

1.6.5 INSPECTION / TESTING

A. PRE-BACKFILL INSPECTION

Before covering:

Foundation/wall

Check for:

- damage;

- unresolved concrete repairs;

- unfinished penetrations.

Waterproofing

Check:

- continuity;

- damage;

- repairs;

- protection board;

- terminations.

Insulation

Check:

- correct product/thickness;

- continuity;

- damage;

- attachment.

Drainage

Check:

- drain installed;

- slope;

- connections;

- stone/filter fabric;

- protection.

Services

Check:

- location;

- joints;

- testing completed where required;

- protection;

- as-built/survey captured.

This stage is extremely important.

B. PLACEMENT

Observe:

- placement method;

- drop height near sensitive work;

- material segregation;

- equipment proximity;

- damage to protection systems;

- uniform placement;

- lift thickness.

C. LIFT CONTROL

Verify:

- lift thickness;

- layer identification;

- proper compaction before next lift;

- testing sequence.

D. COMPACTION

Watch particularly around:

- foundation walls;

- corners;

- drains;

- pipes;

- conduits;

- structures.

Compaction must be adequate without damaging the work.

E. TESTING

Track:

- test location;

- lift;

- required density;

- actual result;

- pass/fail;

- retest.

F. FINAL GRADE

Verify:

- elevation;

- slope;

- drainage away/from structures as required;

- transition to surrounding work.

1.6.6 RECORDS / EVIDENCE

Capture:

- pre-concealment photos;

- waterproofing/drainage acceptance;

- service test records;

- as-built/survey where required;

- material approval;

- lift/test records;

- density results;

- failed/retest results;

- final grade records;

- damage/repair evidence.

1.6.7 NC / DEFICIENCY

Typical issues:

- backfill starts before pre-concealment inspection;

- waterproofing damaged;

- insulation displaced;

- drain crushed;

- wrong backfill material;

- oversized material against structure;

- excessive lift thickness;

- failed density;

- buried service damaged;

- backfill performed before required testing;

- final grade/slope incorrect.

1.6.8 CORRECTIVE ACTION — EXAMPLE

Scenario

During backfill you notice foundation waterproofing has been torn by equipment.

System response:

1. Stop/control affected local area.

2. Photograph damage before further covering.

3. Identify exact location.

4. Notify appropriate field/quality personnel.

5. Obtain/confirm approved repair procedure.

6. Repair membrane.

7. Inspect repaired area.

8. Photograph repair.

9. Reinstate protection.

10. Resume backfill only when release requirements are satisfied.

This is exactly why a quality inspector needs to remain aware during backfill rather than merely reviewing density reports afterward.

1.6.9 VERIFICATION

Verify:

- repairs complete;

- protected systems intact;

- failed density areas reworked;

- retest acceptable;

- services remain intact;

- final grade correct.

1.6.10 CLOSURE

☐ concealed work accepted
☐ photographs/as-builts complete
☐ approved material used
☐ lifts controlled
☐ density tests acceptable
☐ failed tests resolved
☐ waterproofing/insulation/drains protected
☐ services protected
☐ final elevation/slope correct
☐ records complete

1.6.11 REPORTING / ANALYSIS

Track:

- repeated waterproofing damage;

- recurring density failures;

- premature concealment;

- repeated service damage;

- material problems;

- areas repeatedly requiring rework.

Backfill is often where coordination quality becomes more important than individual workmanship.

1.6.12 BACKFILL QUALITY CHECKPOINT

PRE-CONCEALMENT

☐ Foundation accepted
☐ Waterproofing inspected
☐ Insulation inspected
☐ Drainage inspected
☐ Buried services tested
☐ As-builts/survey captured
☐ Photos taken
☐ Outstanding defects resolved

PLACEMENT

☐ Approved material
☐ Correct lift thickness
☐ No damage to adjacent work
☐ Compaction controlled
☐ Testing performed

FINAL

☐ Density accepted
☐ Failed tests resolved
☐ Services intact
☐ Final grade/elevation correct
☐ Drainage slopes correct
☐ Documentation complete

1.7 SITE DRAINAGE

The quality objective is:

Control water during construction and provide permanent drainage that follows the approved grades, structures, routes, and connections without creating ponding, leakage, erosion, or damage to the project.

We need to distinguish:

temporary drainage from permanent drainage.

1.7.1 REQUIREMENTS

🔵 Obtain

- civil/site drainage plans;

- grading plans;

- storm drainage drawings;

- foundation drainage details;

- utility plans;

- profiles;

- structure details;

- drainage specifications;

- pipe/manhole/catch basin specifications;

- geotechnical requirements;

- environmental requirements;

- Plan Qualité;

- PIE/PRIE;

- approved shop drawings;

- approved materials;

- technical changes;

- connection details.

Extract

For each drainage element:

- pipe/material type;

- size;

- class;

- invert elevations;

- slope;

- bedding;

- joint requirements;

- structures;

- inlet/outlet elevation;

- connection location;

- backfill;

- testing;

- inspection requirements;

- final grading.

1.7.2 PLANNING

Temporary drainage

Before work, determine:

- where water will flow;

- where pumps discharge;

- erosion control;

- excavation protection;

- rainfall response;

- protection of subgrade;

- protection of adjacent property/structures.

Permanent drainage

Plan sequence:

layout → excavation → bedding → pipe/structure → connections → testing/inspection → survey/as-built → backfill → final grading

And identify pre-concealment points.

1.7.3 DOCUMENT CONTROL

Verify:

☐ latest drainage plan
☐ correct profile
☐ invert elevations
☐ pipe sizes/materials
☐ structure details
☐ approved shop drawings
☐ current connection details
☐ approved changes incorporated

Drainage errors often come from a small elevation mistake, so profile drawings are critical.

1.7.4 MATERIAL CONTROL

Verify:

- pipe type/class;

- fittings;

- gaskets;

- manhole/catch basin components;

- drain material;

- geotextile;

- granular bedding;

- grates/covers;

- sealants;

- approved manufacturers;

- condition on delivery.

Look for:

- cracked pipe;

- damaged gasket;

- broken precast units;

- contaminated granular;

- incorrect size/class.

1.7.5 INSPECTION / TESTING

A. TEMPORARY DRAINAGE

Observe:

- water accumulation;

- pumps;

- discharge location;

- erosion;

- sediment migration;

- damage to excavation;

- washout;

- effect on adjacent work.

Quality purpose

Temporary drainage protects:

- subgrade;

- excavation bottoms;

- granular;

- concrete preparation;

- stored materials;

- adjacent structures.

B. PERMANENT DRAINAGE — PIPE

Bedding

Verify:

- correct material;

- thickness;

- level/shape;

- no unsuitable material;

- proper support.

Pipe

Check:

- correct type;

- correct diameter;

- condition;

- line;

- grade/slope;

- orientation;

- joints;

- gasket/seals;

- connections;

- support.

Slope

This is crucial.

Too little slope can cause:

- ponding;

- sediment accumulation;

- poor drainage.

Wrong direction is obviously catastrophic.

Use survey/measurement evidence as required.

C. DRAINAGE STRUCTURES

For:

- catch basins;

- manholes;

- sumps;

- drains.

Verify:

- location;

- elevation;

- invert;

- dimensions;

- sections;

- joints;

- connections;

- benching/channel;

- frame/grate elevation;

- accessibility.

D. CONNECTIONS

Verify:

- correct receiving system;

- correct elevation;

- correct fitting;

- sealed joint;

- no interference;

- approved connection method.

E. PRE-BACKFILL INSPECTION

Before concealment:

☐ pipe visible
☐ joints inspected
☐ slope/elevation verified
☐ structures inspected
☐ connections inspected
☐ tests completed where required
☐ photographs complete
☐ survey/as-built complete where required

F. FINAL GRADING

Drainage is not complete just because the underground pipe is correct.

Verify:

- surface slopes;

- positive drainage;

- inlet elevations;

- no ponding;

- interfaces with pavement/landscape/building.

1.7.6 RECORDS / EVIDENCE

Capture:

- pipe material approvals;

- delivery inspection;

- bedding inspection;

- pipe inspection;

- joint/connection photographs;

- structure inspection;

- survey/invert records;

- slope verification;

- test results;

- pre-backfill photos;

- as-built information;

- final grade records.

1.7.7 NC / DEFICIENCY

Typical issues:

- wrong pipe type/size;

- damaged pipe;

- wrong invert elevation;

- insufficient slope;

- reverse slope;

- poor joint;

- incorrect connection;

- inadequate bedding;

- structure at wrong elevation;

- backfill before inspection;

- blocked pipe;

- surface ponding;

- temporary drainage damaging subgrade.

1.7.8 CORRECTIVE ACTION — EXAMPLE

Scenario

Survey shows a section of storm pipe has insufficient slope.

System response:

1. Identify exact chainage/location.

2. Compare actual invert elevations against design.

3. Prevent concealment/backfill if required.

4. Notify field team + Responsable qualité.

5. Determine authorized correction.

Potentially:

- reset pipe;

- adjust bedding;

- revise connection;

but only according to approved direction.

6. Reinstall.

7. Re-survey.

8. Reinspect joints/connections.

9. Record correction.

10. Close only after acceptance.

1.7.9 VERIFICATION

Confirm:

- correct elevation;

- correct slope;

- joints intact;

- connection correct;

- structure remains aligned;

- testing passed;

- no damage during correction.

1.7.10 CLOSURE

Drainage complete when:

☐ approved materials used
☐ layout correct
☐ bedding accepted
☐ pipe size/type correct
☐ slope/inverts correct
☐ joints accepted
☐ structures accepted
☐ connections accepted
☐ required testing passed
☐ as-builts captured
☐ backfill accepted
☐ final surface drainage works
☐ no ponding/erosion issues
☐ records complete

1.7.11 REPORTING / ANALYSIS

Track:

- recurring slope errors;

- structure elevation errors;

- damaged material;

- blocked drainage;

- repeated poor joints;

- repeated ponding;

- drainage-related subgrade failures;

- repeated bypass of pre-backfill inspection.

1.7.12 SITE DRAINAGE QUALITY CHECKPOINT

TEMPORARY

☐ Water controlled
☐ No damaging ponding
☐ No erosion/washout
☐ Discharge appropriate
☐ Subgrade/excavations protected

BEFORE INSTALLATION

☐ Correct drawings
☐ Materials approved
☐ Layout confirmed
☐ Invert/slope requirements known
☐ Bedding requirements known

INSTALLATION

☐ Bedding correct
☐ Pipe correct
☐ Pipe undamaged
☐ Slope correct
☐ Joints correct
☐ Structures correct
☐ Connections correct

PRE-CONCEALMENT

☐ Survey complete
☐ Tests complete
☐ Photos complete
☐ As-built information captured
☐ Deficiencies resolved

FINAL

☐ Backfill accepted
☐ Final grade correct
☐ Positive drainage achieved
☐ No ponding
☐ Records complete

PRACTICAL MULTI-ACTIVITY EXAMPLE

Suppose today's plan is:

07:00 — finish footing excavation
09:00 — geotechnical/subgrade review
11:00 — granular placement
14:00 — underground drain installation
16:00 — partial backfill

A weak inspector sees four unrelated jobs.

Your system sees one controlled sequence:

Excavation → Subgrade → Granular → Drainage → Backfill

and recognizes that every stage creates an acceptance condition for the next one.

Before 07:00

You review:

- today's work;

- current drawings;

- PIE/PRIE;

- required elevations;

- geotechnical requirements;

- granular approval;

- drain details;

- testing requirements.

09:00

Subgrade inspection fails in one area.

Now you immediately understand that:

granular placement cannot simply proceed over that affected area.

You control the interface.

11:00

Granular begins elsewhere.

You track:

- material;

- lift;

- moisture;

- compaction;

- density testing.

14:00

Drain installed.

You verify:

- bedding;

- pipe;

- slope;

- connections.

16:00

Before backfill begins, your brain triggers:

PRE-CONCEALMENT QUALITY GATE

Have you captured:

- pipe photographs?

- invert/survey data?

- test results?

- connections?

- as-built information?

Only then should that buried work disappear from view.

That is exactly why this system will make you more systematic and less reactive.

BUILD 2 — SITEWORK & EARTHWORKS STATUS

1.1 Existing Conditions ✓
1.2 Survey & Layout ✓
1.3 Excavation ✓
1.4 Subgrade ✓
1.5 Granular Materials ✓
1.6 Backfill ✓
1.7 Site Drainage ✓

Section 1 is now structurally complete.

Yes. Let's move into 2. SUBSTRUCTURE, and because these activities are tightly connected, I want to build them as an integrated quality sequence rather than as isolated pages.

The logic is:

Foundation Formwork → Reinforcement → Embedded Items → Pre-Pour Gate → Foundation Concrete → Post-Pour Acceptance → Foundation Walls → Slab-on-Grade → Waterproofing → Insulation → Drainage → Backfill Against Structure

The same rule applies throughout: CRT/Hydro-Québec project documents govern; this playbook guides your execution so nothing gets missed.

2. SUBSTRUCTURE

2.1 FOUNDATION FORMWORK

Quality objective

Create formwork that produces the required foundation geometry, position, elevation, finish, openings and interfaces, while remaining stable through concrete placement.

01 — REQUIREMENTS

🔵 Obtain:

- latest structural foundation drawings;

- formwork-related details;

- foundation dimensions;

- sections/elevations;

- concrete specifications;

- tolerances from project documents;

- architectural/interface drawings where relevant;

- approved shop drawings if any;

- Plan Qualité;

- applicable PIE/PRIE;

- approved execution procedures;

- technical directives;

- QMT/RFI responses;

- latest revisions.

Extract:

- footing/wall dimensions;

- top/bottom elevations;

- offsets;

- chamfers;

- keyways;

- recesses;

- construction joints;

- openings;

- embedded interfaces;

- finish requirements;

- allowable tolerances;

- required inspection/hold points.

02 — PLANNING

Before formwork installation, determine:

- which footing/wall is being formed;

- sequence of pour;

- formwork completion time;

- reinforcement installation timing;

- embed installation timing;

- pre-pour inspection timing;

- concrete arrival time;

- who must inspect before pour;

- which surfaces will become inaccessible after reinforcement/embeds.

Ask:

What must be verified now before other trades make it harder to inspect?

03 — DOCUMENT CONTROL

Verify:

☐ latest foundation drawing
☐ latest section/detail
☐ latest dimensions/elevations
☐ latest technical changes
☐ current PIE/PRIE
☐ current procedure
☐ superseded drawings removed from use

04 — MATERIAL CONTROL

Check where relevant:

- form panels condition;

- form ties;

- supports/bracing;

- release agent;

- waterstops;

- chamfer strips;

- joint materials;

- temporary openings;

- blockouts.

For permanent embedded formwork/components, verify approvals.

05 — INSPECTION / TESTING

Before reinforcement

Check:

- location/grid;

- dimensions;

- orientation;

- elevation;

- alignment;

- squareness where relevant;

- form cleanliness;

- base condition;

- stability;

- openings/blockouts;

- keyways;

- joint locations.

Before concrete placement

Recheck:

- dimensions after reinforcement installation;

- form movement/deformation;

- bracing;

- tightness;

- cleanliness;

- standing water/debris;

- openings;

- embeds;

- waterstops;

- construction-joint preparation.

06 — RECORDS / EVIDENCE

Capture:

- footing/wall ID;

- drawing/detail reference;

- form dimensions;

- elevation verification;

- photographs;

- inspection form;

- marked-up drawing where useful;

- discrepancy/correction records;

- pre-pour status.

07 — NC / DEFICIENCY

Common issues:

- wrong dimensions;

- wrong elevation;

- misalignment;

- unstable formwork;

- missing blockout;

- wrong opening;

- damaged/dirty forms;

- missing keyway;

- water/debris inside form;

- incorrect joint location.

08 — CORRECTIVE ACTION

Example: wall form set 40 mm out of line.

Identify → measure → document → compare to requirement → control pour → correct form → remeasure → reinspect → record release.

09 — VERIFICATION

Confirm:

- corrected dimensions;

- alignment;

- elevation;

- stability;

- no secondary impact on reinforcement/embeds.

10 — CLOSURE

☐ geometry correct
☐ elevation correct
☐ alignment correct
☐ openings correct
☐ joint features correct
☐ form stable
☐ clean
☐ records complete
☐ ready for pre-pour release

11 — REPORTING / ANALYSIS

Track recurring:

- dimensional errors;

- form movement;

- dirty forms;

- missing blockouts;

- late changes;

- repeated rework.

12 — QUALITY CHECKPOINT

BEFORE REBAR

☐ Grid correct
☐ Dimensions correct
☐ Elevation correct
☐ Forms stable
☐ Openings/blockouts correct

PRE-POUR

☐ No debris/water
☐ Forms still aligned
☐ Joints/waterstops correct
☐ Embeds coordinated
☐ Pre-pour inspection ready

2.2 FOUNDATION REINFORCEMENT

Quality objective

Install the correct reinforcement, in the correct quantity, position, spacing, lap and cover, with adequate support so that it remains compliant during concrete placement.

01 — REQUIREMENTS

🔵 Obtain:

- structural drawings;

- reinforcement details;

- bar schedules;

- approved shop drawings;

- specifications;

- applicable standards referenced by project;

- lap/splice requirements;

- cover requirements;

- anchorage details;

- dowel details;

- mechanical coupler approvals if used;

- PIE/PRIE;

- technical changes;

- RFIs/QMTs.

Extract:

- bar mark;

- diameter;

- grade;

- quantity;

- spacing;

- location;

- top/bottom mat;

- lap length;

- development/anchorage;

- hook type;

- cover;

- chairs/supports;

- dowels;

- splice locations.

02 — PLANNING

Before inspection:

- identify the exact footing/wall/slab;

- obtain bar schedule/shop drawing;

- know what will be concealed by concrete;

- coordinate with formwork and embeds;

- identify congested zones;

- identify critical laps/anchors;

- schedule pre-pour inspection before concrete arrival.

03 — DOCUMENT CONTROL

Verify:

☐ latest reinforcement drawing
☐ latest shop drawing
☐ current bar schedule
☐ revised details incorporated
☐ approved coupler/material data available
☐ current PIE/PRIE

04 — MATERIAL CONTROL

Verify:

- bar size;

- grade;

- identification;

- mill certificates where required;

- bar condition;

- corrosion/contamination limits per project requirements;

- couplers;

- chairs/spacers;

- tie wire;

- dowels.

05 — INSPECTION / TESTING

Check systematically:

Bar identification

- correct size;

- correct grade;

- correct bar mark.

Quantity and spacing

- number of bars;

- center-to-center spacing;

- top/bottom layers.

Position

- correct elevation;

- correct face;

- correct orientation.

Cover

- bottom cover;

- side cover;

- top cover;

- proper spacers/chairs.

Laps and splices

- required length;

- location;

- staggering where required;

- coupler installation where applicable.

Anchorage

- hooks;

- development;

- dowels;

- embedment.

Supports

- chairs stable;

- bars secured;

- reinforcement won't shift during pour.

Cleanliness

- excessive mud;

- oil;

- concrete splatter;

- debris.

06 — RECORDS / EVIDENCE

Capture:

- element ID;

- bar marks;

- critical measurements;

- cover checks;

- lap/splice checks;

- photographs;

- inspection checklist;

- approved shop-drawing reference;

- corrections/reinspection.

07 — NC / DEFICIENCY

Common issues:

- wrong bar size;

- missing bars;

- wrong spacing;

- insufficient cover;

- short lap;

- misplaced dowels;

- wrong orientation;

- unsupported reinforcement;

- unapproved couplers;

- reinforcement shifted by other trades.

08 — CORRECTIVE ACTION

Example: footing requires 75 mm cover but observed cover is 35 mm.

Measure → document → control pour → reposition/support reinforcement → remeasure → photograph → close.

If discovered after concrete placement, do not improvise. Escalate for authorized technical disposition.

09 — VERIFICATION

Recheck:

- corrected position;

- cover;

- lap;

- stability;

- impact on embeds/openings.

10 — CLOSURE

☐ correct bars
☐ correct quantity
☐ spacing correct
☐ cover correct
☐ laps/splices correct
☐ anchorage correct
☐ dowels correct
☐ stable/supports adequate
☐ clean
☐ records complete

11 — REPORTING / ANALYSIS

Track:

- repeated cover problems;

- missing bars;

- shop-drawing confusion;

- congested details;

- repeated rebar displacement;

- coupler issues.

12 — QUALITY CHECKPOINT

☐ Latest drawing
☐ Correct bars
☐ Correct spacing
☐ Correct cover
☐ Correct laps
☐ Correct anchorage
☐ Dowels correct
☐ Reinforcement stable
☐ No unresolved conflicts
☐ Pre-pour record complete

2.3 EMBEDDED ITEMS

Quality objective

Ensure every item that must be cast into or pass through the concrete is approved, correctly located, correctly oriented and secured before the pour.

This is critical because missing or misplaced embeds are much harder to fix after concrete placement.

01 — REQUIREMENTS

🔵 Obtain:

- structural drawings;

- architectural drawings;

- mechanical drawings;

- electrical drawings;

- equipment drawings;

- approved shop drawings;

- embed schedules;

- anchor-bolt plans;

- sleeve/opening details;

- waterstop details;

- equipment base details;

- PIE/PRIE;

- technical changes;

- coordination drawings/BIM if used.

02 — PLANNING

Before pour:

- identify all trades touching the concrete;

- coordinate structural + mechanical + electrical + architectural inputs;

- identify embedded plates, bolts, sleeves, conduits, openings, drains, waterstops;

- verify who owns each item;

- establish pre-pour signoff responsibility.

03 — DOCUMENT CONTROL

Check:

☐ structural revision
☐ MEP revisions
☐ equipment/shop drawings
☐ coordination drawings
☐ approved technical changes
☐ current embed schedule

04 — MATERIAL CONTROL

Verify:

- anchor type;

- plate size;

- sleeve type;

- conduit;

- insert;

- waterstop;

- product approval;

- condition;

- identification.

05 — INSPECTION / TESTING

Check:

- exact location;

- elevation;

- orientation;

- projection;

- spacing;

- edge distance where specified;

- anchorage;

- secure fixing;

- relationship to rebar;

- conflict-free installation;

- opening dimensions;

- waterstop continuity/joints.

06 — RECORDS / EVIDENCE

Capture:

- embed ID;

- location/grid;

- reference drawing;

- measured position;

- photographs;

- anchor-bolt survey if required;

- inspection record;

- corrections.

07 — NC / DEFICIENCY

Typical:

- missing sleeve;

- misplaced anchor bolt;

- wrong projection;

- embed conflicts with rebar;

- missing waterstop;

- unsecured conduit;

- wrong opening dimension;

- late field change not incorporated.

08 — CORRECTIVE ACTION

Example: anchor bolt found 25 mm off location before pour.

Measure → document → compare to approved detail → reposition → secure → re-survey/recheck → record.

After concrete? Escalate for engineering disposition.

09 — VERIFICATION

Confirm corrected:

- location;

- elevation;

- orientation;

- stability;

- clearance;

- interface.

10 — CLOSURE

☐ all embeds identified
☐ all locations verified
☐ all elevations verified
☐ all items secured
☐ conflicts resolved
☐ waterstops complete
☐ evidence complete

11 — REPORTING / ANALYSIS

Track:

- repeated missed sleeves;

- anchor-bolt errors;

- trade coordination failures;

- late MEP changes;

- embed clashes.

12 — QUALITY CHECKPOINT

☐ Structural embeds
☐ Mechanical sleeves/openings
☐ Electrical conduits/inserts
☐ Anchor bolts
☐ Plates/inserts
☐ Waterstops
☐ Blockouts
☐ All secured
☐ No unresolved clashes
☐ Pre-pour evidence complete

2.4 PRE-POUR QUALITY GATE

This deserves its own system even though it sits between modules.

Objective

Do not allow concrete placement until all prerequisite quality conditions are satisfied or formally released according to project procedure.

Pre-pour master checklist

Documents

☐ Latest drawings
☐ Latest shop drawings
☐ Latest technical changes
☐ PIE/PRIE reviewed
☐ Approved mix available
☐ Required procedures approved

Formwork

☐ Dimensions
☐ Elevations
☐ Alignment
☐ Stability
☐ Cleanliness
☐ Openings/joints

Reinforcement

☐ Bar size
☐ Quantity
☐ Spacing
☐ Cover
☐ Laps
☐ Anchorage
☐ Stability

Embeds

☐ Anchors
☐ Sleeves
☐ Inserts
☐ Conduits
☐ Plates
☐ Waterstops
☐ Openings

Site conditions

☐ Base/substrate accepted
☐ Water/debris removed
☐ Access ready
☐ Weather reviewed
☐ Cold/hot weather controls ready if required

Testing

☐ Lab notified
☐ Sampling requirements known
☐ Test equipment ready
☐ Cylinder/sample identification plan ready

Communication

☐ Required parties notified
☐ Hold/witness points satisfied
☐ Outstanding deficiencies cleared
☐ Release obtained where required

Only then:

POUR READY

2.5 FOUNDATION CONCRETE

Quality objective

Place the approved concrete in the correct location, under controlled conditions, using the required testing, placement, consolidation, finishing and curing processes, with full traceability.

01 — REQUIREMENTS

🔵 Obtain:

- structural drawings;

- concrete specification;

- approved mix design;

- PIE/PRIE;

- testing requirements;

- placement procedure;

- hot/cold weather procedure;

- curing requirements;

- joint details;

- finish requirements;

- delivery limits;

- strength requirements;

- technical changes.

Extract:

- concrete class;

- strength;

- exposure class;

- slump range;

- air requirement if applicable;

- temperature limits;

- max water/cement ratio where applicable;

- admixtures;

- delivery/discharge time limits;

- sampling frequency;

- curing method;

- finish;

- joint locations.

02 — PLANNING

Before pour:

- pour sequence;

- quantity;

- truck sequence;

- pump/access;

- manpower;

- vibrator availability;

- backup equipment;

- lab/testing;

- weather;

- curing materials;

- joint strategy;

- emergency/stop-pour plan.

03 — DOCUMENT CONTROL

Verify:

☐ approved mix
☐ current pour drawing
☐ current procedure
☐ current PIE/PRIE
☐ current technical directives
☐ correct test requirements

04 — MATERIAL CONTROL

Verify on delivery:

- supplier;

- mix ID;

- batch ticket;

- truck number;

- batch time;

- admixtures;

- water additions;

- quantity;

- consistency with approved mix.

🟠 Any field water addition must follow project/specification requirements. Do not casually accept undocumented water addition.

05 — INSPECTION / TESTING

Delivery

Check:

- ticket;

- mix designation;

- time;

- condition.

Fresh concrete tests where required

- temperature;

- slump;

- air content;

- unit weight;

- cylinders/samples;

- other specified tests.

Placement

Observe:

- placement location;

- sequence;

- free fall/control where relevant;

- segregation;

- lift depth;

- placement continuity;

- rebar/embeds not displaced;

- formwork behavior.

Consolidation

Observe:

- vibrator use;

- adequate consolidation;

- over-vibration avoided;

- corners/around embeds addressed.

Finishing

Verify specified finish.

Joints

Check construction-joint location and preparation.

Curing

Verify:

- method;

- timing;

- duration;

- protection;

- environmental conditions.

06 — RECORDS / EVIDENCE

Maintain:

- pour ID;

- element/location;

- date/time;

- approved mix;

- delivery tickets;

- truck numbers;

- test results;

- cylinder IDs;

- weather;

- start/end time;

- photographs;

- observations;

- interruptions;

- corrective actions;

- curing record.

This should allow full traceability:

Element → concrete batch/trucks → tests → cylinders → strength results

07 — NC / DEFICIENCY

Potential issues:

- wrong mix;

- out-of-range slump;

- temperature issue;

- air issue;

- excessive delay;

- unauthorized water addition;

- segregation;

- honeycombing risk;

- form movement;

- displaced rebar/embed;

- cold joint;

- incomplete consolidation;

- inadequate curing.

08 — CORRECTIVE ACTION

Example: slump result outside specified range.

System:

Hold acceptance of affected load as required → verify test → compare to project criterion → notify appropriate quality/site authority → determine disposition per project procedure → document load status → accept/reject/other authorized disposition → retain record.

Do not personally invent acceptance criteria.

09 — VERIFICATION

Verify:

- placement completed;

- curing applied;

- no immediate obvious issues;

- test records complete;

- cylinders properly identified/stored;

- rejected/affected loads documented.

10 — CLOSURE

Pour record complete when:

☐ all tickets collected
☐ tests recorded
☐ samples identified
☐ placement observations documented
☐ curing started
☐ issues controlled
☐ photos filed
☐ strength results tracked for later acceptance

Important: concrete placement may be physically complete while quality acceptance remains open pending test results.

11 — REPORTING / ANALYSIS

Track:

- rejected loads;

- recurring slump variation;

- temperature issues;

- repeated form movement;

- recurring honeycombing;

- supplier variability;

- strength-test trends;

- curing problems.

12 — QUALITY CHECKPOINT

BEFORE POUR

☐ Pre-pour gate complete

DELIVERY

☐ Correct mix
☐ Tickets verified
☐ Time acceptable
☐ Required tests performed

DURING POUR

☐ Placement controlled
☐ Consolidation adequate
☐ Rebar/embeds stable
☐ Forms stable
☐ Joints controlled

AFTER POUR

☐ Finish acceptable
☐ Curing applied
☐ Samples identified
☐ Records complete
☐ Issues tracked

2.6 FOUNDATION CONCRETE ACCEPTANCE

Quality objective

Verify that the completed concrete meets geometric, surface, structural-test and project-quality requirements before subsequent work relies on it.

01 — REQUIREMENTS

Obtain:

- drawings;

- concrete specifications;

- finish requirements;

- tolerances;

- strength requirements;

- repair procedures;

- test acceptance requirements;

- professional directives;

- PIE/PRIE.

02 — PLANNING

Plan inspection after:

- appropriate form removal;

- safe access;

- test results becoming available;

- before waterproofing/backfill/steel erection/etc.

03 — DOCUMENT CONTROL

Verify current:

- drawings;

- repair procedures;

- acceptance criteria;

- test results.

04 — MATERIAL CONTROL

If repair materials are needed:

- approved repair mortar;

- grout;

- epoxy;

- coating;

- curing products.

05 — INSPECTION / TESTING

Check:

Geometry

- dimensions;

- elevation;

- alignment;

- plumbness;

- anchor positions;

- openings.

Surface

- honeycombing;

- voids;

- bugholes where relevant;

- cracks;

- spalling;

- exposed reinforcement;

- fins;

- laitance;

- damage.

Joints

- condition;

- keyways;

- waterstops;

- construction-joint quality.

Test results

- compressive strength;

- other specified results.

06 — RECORDS / EVIDENCE

Capture:

- inspection report;

- defect map;

- photographs;

- measurements;

- test results;

- repair records;

- reinspection evidence;

- annotated drawings.

07 — NC / DEFICIENCY

Potential:

- honeycombing;

- cracking;

- exposed bar;

- dimensional error;

- failed strength;

- misplaced anchors;

- voids;

- unacceptable surface;

- damaged edge;

- wrong elevation.

08 — CORRECTIVE ACTION

Example: honeycombing found after form removal.

Identify extent → photograph → classify/report per CRT process → obtain approved repair method where required → surface preparation → repair → cure → reinspect → close.

Do not treat all honeycombing the same. Severity and structural significance require appropriate technical judgment.

09 — VERIFICATION

Check:

- repair area;

- approved method followed;

- material used;

- finished surface;

- curing;

- required testing;

- documentation.

10 — CLOSURE

☐ geometry acceptable
☐ surface issues addressed
☐ strength results acceptable
☐ repairs closed
☐ anchors/openings verified
☐ next work can proceed
☐ records complete

11 — REPORTING / ANALYSIS

Trend:

- recurring honeycombing;

- repeated cracks;

- dimensional errors;

- strength variability;

- recurring form leakage;

- problem locations.

12 — QUALITY CHECKPOINT

☐ Form removed sufficiently for inspection
☐ Surface inspected
☐ Dimensions checked
☐ Anchors/openings checked
☐ Test results reviewed
☐ Deficiencies documented
☐ Repairs verified
☐ Acceptance complete

2.7 FOUNDATION WALLS

For foundation walls, use the same core controls as concrete, but pay additional attention to:

- vertical alignment/plumbness;

- wall thickness;

- penetrations;

- waterstops;

- construction joints;

- openings;

- embedded plates;

- ties;

- waterproofing substrate condition.

The workflow is:

Formwork → Rebar → Embeds → Pre-pour → Concrete → Acceptance

with wall-specific checks layered in.

2.8 SLAB-ON-GRADE

Key workflow

Subgrade → granular → insulation → vapour barrier → reinforcement → embeds → pre-pour → concrete → finish → joints → curing → acceptance

Critical checks:

- subbase acceptance;

- slab thickness;

- vapour barrier continuity;

- insulation thickness;

- reinforcement position;

- sleeves/drains/embeds;

- elevation;

- slopes;

- floor flatness/levelness if specified;

- joints;

- curing;

- surface defects.

This should eventually become its own full module because slabs can have many interfaces.

2.9 BELOW-GRADE WATERPROOFING

Quality objective

Create a continuous, properly terminated and protected waterproofing system before it becomes concealed by insulation/protection/backfill.

Critical items:

- substrate condition;

- approved membrane;

- primer;

- temperature/weather;

- continuity;

- seams/laps;

- corners;

- penetrations;

- terminations;

- tie-hole repairs;

- membrane damage;

- protection board;

- pre-backfill inspection.

This is one of the strongest pre-concealment workflows in the entire substructure.

2.10 FOUNDATION INSULATION

Check:

- approved product;

- thickness;

- location;

- continuity;

- attachment;

- joints;

- gaps;

- damage;

- compatibility with waterproofing;

- protection before backfill.

2.11 FOUNDATION DRAINAGE

Check:

- approved drain;

- location;

- elevation;

- slope;

- connections;

- granular surround;

- geotextile;

- cleanouts;

- outlet;

- protection;

- pre-backfill evidence.

2.12 BACKFILL AGAINST STRUCTURE

This uses our 1.6 Backfill workflow but adds a key interface question:

Will the backfill operation damage anything we just accepted?

Before backfill:

☐ concrete accepted
☐ waterproofing accepted
☐ insulation accepted
☐ drainage accepted
☐ services accepted
☐ photos/as-builts complete

During backfill:

☐ approved material
☐ controlled lift thickness
☐ equipment distance/control
☐ no membrane damage
☐ no insulation displacement
☐ no drain damage
☐ compaction/testing performed

THE SUBSTRUCTURE MASTER GATE

Before calling the substructure quality scope complete, I want a master check:

Geometry

☐ Excavation correct
☐ Foundation position correct
☐ Elevations correct
☐ Walls/slabs correct

Structure

☐ Formwork accepted
☐ Reinforcement accepted
☐ Embeds accepted
☐ Concrete accepted
☐ Strength results accepted

Moisture protection

☐ Waterproofing accepted
☐ Insulation accepted
☐ Drainage accepted

Interfaces

☐ MEP penetrations correct
☐ Anchors/inserts correct
☐ Future structural interfaces correct

Concealed work

☐ Pre-concealment photos complete
☐ As-builts/survey complete
☐ Test records complete

Deficiencies/NC

☐ Open items controlled
☐ Corrective actions verified
☐ Required closures complete

Records

☐ Inspection records complete
☐ Test records complete
☐ Photos traceable
☐ Document references current
☐ Responsable qualité updated

That is the point where:

SUBSTRUCTURE QUALITY = CONTROLLED, TRACEABLE, AND READY FOR SUPERSTRUCTURE

Yes. We’ll keep the same field-operating structure and take Superstructure to the same depth as Sitework/Substructure.

The governing principle stays:

CRT/Hydro-Québec drawings, devis, Plan Qualité, PIE/PRIE, approved shop drawings, procedures, technical directives, professional instructions, and applicable standards govern.
This playbook ensures that you systematically find the requirements, plan the inspection, control materials/documents, inspect, record evidence, manage deviations, verify corrective work, and close the quality loop.

3. SUPERSTRUCTURE

The quality objective for the superstructure is:

Ensure that the building’s primary structural systems are constructed from approved materials, in the correct location and geometry, using approved installation methods, with required inspection/testing evidence, so that loads can be transferred safely through the completed structure as designed.

3.1 CAST-IN-PLACE CONCRETE

This uses much of the foundation-concrete logic, but superstructure concrete introduces additional concerns such as elevated work, columns, beams, walls, suspended slabs, construction sequencing, dimensional accumulation, temporary supports, penetrations, and interfaces with future steel/MEP/envelope systems.

3.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain

- latest structural IFC drawings;

- concrete plans and sections;

- column/wall schedules;

- beam/slab details;

- reinforcement drawings;

- approved reinforcement shop drawings;

- embed/anchor drawings;

- architectural interface drawings;

- mechanical/electrical penetration drawings;

- approved coordination/BIM drawings where applicable;

- concrete specifications;

- reinforcement specifications;

- formwork specifications;

- approved concrete mix designs;

- approved execution/method procedures;

- temporary-support/shoring information where applicable;

- Plan Qualité;

- applicable PIE/PRIE;

- hot/cold weather procedures;

- curing requirements;

- technical directives;

- QMT/RFI responses;

- latest approved revisions.

Extract specifically

For every pour:

- element ID;

- grid/location;

- member dimensions;

- elevations;

- slab thickness;

- beam/column/wall size;

- concrete class/strength;

- exposure requirements;

- finish requirements;

- rebar size/spacing;

- cover;

- laps/splices;

- anchor/insert positions;

- openings;

- construction joints;

- embedded MEP;

- required testing;

- hold/witness points;

- curing requirements;

- stripping/shoring requirements.

3.1.2 PLANNING

Before the work starts, understand the sequence:

formwork → reinforcement → embeds/openings → pre-pour → concrete placement → testing → curing → stripping → post-pour inspection

Plan around the actual construction schedule.

Ask:

- What is being poured?

- When?

- What is concealed afterward?

- Which preceding work must already be accepted?

- Which inspection points are mandatory?

- Which professional/laboratory personnel must attend?

- What MEP interfaces exist?

- What future structural steel/equipment interfaces rely on this pour?

- Is there temporary shoring/re-shoring that affects the quality sequence?

Critical superstructure planning issue

A dimension error on Level 1 may propagate upward.

So verify:

grid → elevation → column/wall location → slab edge → embeds → next-level interface

rather than treating each pour in isolation.

3.1.3 DOCUMENT CONTROL

Before inspection:

☐ correct floor/zone
☐ current structural drawing
☐ current reinforcement shop drawing
☐ current embed/opening drawing
☐ latest architectural interface
☐ latest MEP coordination
☐ current concrete mix approval
☐ current method statement
☐ latest technical changes incorporated
☐ current PIE/PRIE

🟠 Example

A revised electrical equipment room requires a new floor opening.

The old structural drawing does not show it, but an approved technical change does.

If the pour proceeds using the old layout, you may end up saw-cutting structural concrete later.

So:

technical change control before pour is critical.

3.1.4 MATERIAL CONTROL

Verify:

Concrete

- approved mix;

- supplier;

- mix ID;

- delivery ticket;

- admixtures;

- batch time;

- concrete class.

Reinforcement

- bar type;

- size;

- grade;

- condition;

- certification where required;

- couplers;

- chairs/spacers.

Embedded materials

- anchor bolts;

- inserts;

- plates;

- sleeves;

- conduits;

- waterstops where applicable;

- proprietary components.

Formwork/interface materials

- approved release agents;

- joint materials;

- curing products;

- repair materials where applicable.

3.1.5 INSPECTION / TESTING

A. FORMWORK

Check:

- grid/location;

- member dimensions;

- elevation;

- slab edges;

- openings;

- beam drops;

- column/wall alignment;

- form tightness;

- cleanliness;

- stability;

- joints;

- chamfers;

- blockouts;

- required temporary support interfaces.

B. REINFORCEMENT

Check:

- correct bars;

- quantity;

- spacing;

- layer;

- cover;

- lap/splice;

- couplers;

- anchorage;

- dowels;

- stirrups/ties;

- chair/support stability;

- congested zones;

- cleanliness.

C. EMBEDS / OPENINGS

Check:

- anchor bolts;

- inserts;

- base plates;

- sleeves;

- electrical conduits;

- mechanical penetrations;

- drains;

- blockouts;

- openings;

- edge distances;

- location/elevation;

- fixing/stability.

D. PRE-POUR QUALITY GATE

Confirm:

☐ all prerequisite inspections complete
☐ unresolved issues controlled
☐ correct documents available
☐ lab notified
☐ approved mix confirmed
☐ testing requirements known
☐ weather acceptable
☐ curing materials ready
☐ required releases obtained

E. CONCRETE PLACEMENT

Observe:

- correct mix arriving;

- ticket verification;

- discharge time;

- placement sequence;

- segregation;

- consolidation;

- forms/rebar/embeds remaining stable;

- slab thickness/elevation control;

- finishing;

- construction joints;

- interruptions;

- environmental conditions.

F. TESTING

Where specified:

- slump;

- air;

- concrete temperature;

- cylinders;

- other required fresh concrete tests;

- sample identification;

- test frequency.

G. CURING

Verify:

- curing starts at required time;

- approved method;

- adequate coverage;

- duration;

- moisture/protection;

- temperature control;

- protection from traffic/damage.

H. POST-POUR

Inspect after stripping/access:

- dimensions;

- elevation;

- alignment;

- surface condition;

- honeycombing;

- voids;

- cracks;

- exposed reinforcement;

- anchor positions;

- openings;

- slab edges;

- damaged areas;

- test results when available.

3.1.6 RECORDS / OBJECTIVE EVIDENCE

For each concrete element/pour, retain:

- pour ID;

- date;

- location/grid;

- drawing references;

- approved mix;

- pre-pour inspection;

- photos before pour;

- delivery tickets;

- testing records;

- cylinder/sample IDs;

- weather data where required;

- placement notes;

- curing records;

- post-pour photos;

- defects;

- NCR/deficiency records;

- repair records;

- strength results;

- final acceptance status.

Traceability target

You should be able to answer:

Which concrete went into this exact column/slab/wall, which tests correspond to it, what issues occurred, and how were they resolved?

3.1.7 NC / DEFICIENCY

Common issues:

- wrong concrete mix;

- wrong slab thickness;

- wrong elevation;

- missing rebar;

- insufficient cover;

- misplaced embed;

- missed sleeve;

- wrong opening;

- form movement;

- cold joint;

- honeycombing;

- cracking;

- failed strength;

- poor curing;

- out-of-tolerance column/wall;

- anchor bolt mislocation;

- unapproved field change.

3.1.8 CORRECTIVE ACTION — PRACTICAL EXAMPLE

Scenario

After stripping a wall, you observe severe honeycombing around a congested reinforcement zone.

Process:

- Identify exact wall/grid/elevation.

- Photograph overview + close-up.

- Determine extent.

- Reference drawing/specification.

- Inform Responsable qualité/site personnel.

- Prevent concealment/coating if needed.

- Obtain approved repair disposition.

- Verify repair-material approval.

- Observe/inspect surface preparation.

- Inspect completed repair.

- Retain repair evidence.

- Close only after required acceptance.

Do not assume every honeycombed area is a cosmetic patch.

3.1.9 VERIFICATION

After correction/rework:

- inspect corrected geometry;

- confirm reinforcement/anchors if exposed;

- verify approved repair method;

- verify repair material;

- verify curing;

- review test results;

- remeasure if dimensional issue;

- photograph final condition.

3.1.10 CLOSURE

☐ Geometry accepted
☐ Reinforcement record complete
☐ Embeds/openings accepted
☐ Concrete testing complete
☐ Strength accepted
☐ Surface issues resolved
☐ Repairs closed
☐ Curing records complete
☐ Final inspection complete
☐ Next activity can proceed

3.1.11 REPORTING / ANALYSIS

Track trends such as:

- repeated honeycombing;

- low cover;

- missed embeds;

- late drawing revisions;

- recurring cylinder-strength issues;

- recurring slab-elevation errors;

- repeated rebar congestion;

- formwork movement;

- poor curing practices.

These trends can reveal process failures upstream.

3.1.12 FIELD QUALITY CHECKPOINT

PRE-POUR

☐ Correct drawings
☐ Formwork accepted
☐ Rebar accepted
☐ Embeds/openings accepted
☐ Mix approved
☐ Testing coordinated
☐ Hold points cleared

POUR

☐ Correct tickets
☐ Required tests
☐ Placement controlled
☐ Consolidation controlled
☐ Forms stable
☐ Embeds stable
☐ Finish correct

POST-POUR

☐ Curing
☐ Surface inspection
☐ Geometry
☐ Test results
☐ Deficiencies tracked
☐ Repairs verified
☐ Final acceptance

3.2 STRUCTURAL STEEL — MATERIALS

Quality objective

Ensure that every structural-steel member, connection component and related material delivered to site is the correct approved product, identifiable, traceable, undamaged and properly stored before erection.

3.2.1 REQUIREMENTS

🔵 Obtain:

- structural steel drawings;

- approved fabrication/shop drawings;

- erection drawings;

- connection details;

- steel specifications;

- bolt specifications;

- welding requirements;

- coating/galvanizing requirements;

- mill certificate requirements;

- fabrication inspection records;

- approved substitutions;

- PIE/PRIE;

- technical directives;

- RFI/QMT responses.

Extract:

- member mark;

- steel grade;

- section;

- plate thickness;

- bolt grade;

- weld requirements;

- coating/galvanizing;

- certification requirements;

- inspection requirements.

3.2.2 PLANNING

Before steel arrives:

- know delivery sequence;

- determine storage area;

- ensure members can be identified;

- determine whether fabrication records must be reviewed before erection;

- identify damaged-member escalation process;

- coordinate erection drawings and survey control.

3.2.3 DOCUMENT CONTROL

Verify:

☐ approved shop drawings
☐ current erection drawings
☐ approved connection details
☐ approved steel grades
☐ latest revisions
☐ fabrication changes approved
☐ required certificates available

3.2.4 MATERIAL CONTROL

On receipt, verify:

Member identification

- member mark;

- section/size;

- plate/member type;

- location assignment.

Certification

- mill certificates where required;

- fabrication records;

- galvanizing/coating certificates;

- welding/NDT records from fabrication where applicable.

Condition

Look for:

- bent members;

- twisted flanges;

- damaged holes;

- cracks;

- damaged welds;

- coating damage;

- excessive corrosion;

- transport damage.

Storage

Verify:

- proper support;

- separation from ground;

- drainage;

- protection;

- identification retained;

- members not distorted by poor stacking.

3.2.5 INSPECTION / TESTING

Check delivered steel against:

shop drawing → member mark → actual member

Potential verification:

- member dimensions;

- connection plates;

- hole patterns;

- stiffeners;

- welded attachments;

- coating condition;

- galvanizing;

- identification.

3.2.6 RECORDS / EVIDENCE

Maintain:

- delivery records;

- member identification;

- certificates;

- receiving-inspection photos;

- damaged-member records;

- fabrication NCRs where relevant;

- coating/galvanizing records;

- storage observations.

3.2.7 NC / DEFICIENCY

Common:

- wrong member;

- missing member mark;

- missing certificate;

- damaged flange/web;

- bent member;

- wrong hole pattern;

- damaged galvanizing;

- unapproved field modification;

- unidentified material.

3.2.8 CORRECTIVE ACTION — EXAMPLE

A beam arrives with visible flange deformation.

Do not erect first and “see if it fits.”

System:

Identify member → photograph → compare shop drawing → quarantine/control if required → notify → obtain disposition → repair/replace as authorized → reinspect → close.

3.2.9 VERIFICATION

Confirm:

- repaired/replacement member identified;

- geometry acceptable;

- coating restored;

- certificates complete;

- approval/disposition documented.

3.2.10 CLOSURE

☐ Correct member
☐ Identification traceable
☐ Certifications complete
☐ Condition acceptable
☐ Coating acceptable
☐ Storage acceptable
☐ Any damage resolved
☐ Ready for erection

3.2.11 REPORTING / ANALYSIS

Track:

- repeated shipping damage;

- missing certificates;

- recurring fabrication errors;

- coating defects;

- wrong member deliveries.

3.2.12 QUALITY CHECKPOINT

☐ Member mark
☐ Steel grade
☐ Shop drawing match
☐ Certificates
☐ Geometry
☐ Welded attachments
☐ Hole patterns
☐ Coating
☐ Damage
☐ Storage
☐ Release for erection

3.3 STRUCTURAL STEEL — ERECTION

Quality objective

Erect each member in the correct location, orientation, elevation and alignment, with stable temporary conditions and complete compliant connections.

3.3.1 REQUIREMENTS

Obtain:

- erection drawings;

- approved shop drawings;

- structural plans;

- grid/elevation data;

- connection details;

- temporary bracing requirements;

- erection procedure;

- anchor survey;

- bolt/weld requirements;

- PIE/PRIE;

- technical changes.

3.3.2 PLANNING

Before erection:

- verify concrete foundations/supports accepted;

- verify anchor bolts;

- review erection sequence;

- identify temporary bracing requirements;

- ensure survey control;

- know inspection hold points;

- coordinate crane/access constraints;

- know which connections are temporary vs final.

3.3.3 DOCUMENT CONTROL

Verify:

☐ latest erection drawing
☐ latest member marks
☐ approved connection details
☐ anchor survey
☐ technical changes incorporated
☐ current bolt/weld requirements

3.3.4 MATERIAL CONTROL

Verify before lift:

- correct member;

- damage-free;

- connection materials available;

- bolts correct;

- base plates/shims;

- coating condition.

3.3.5 INSPECTION / TESTING

Member location

- correct grid;

- correct bay;

- correct elevation.

Orientation

- member rotated correctly;

- connection plates correct side;

- camber/orientation where specified.

Alignment

- line;

- level;

- fit-up.

Plumbness

Particularly:

- columns;

- frames;

- vertical bracing.

Elevation

Verify:

- base plate;

- beam elevation;

- floor/interface level.

Temporary bracing

Check:

- installed as required;

- retained until structure stable;

- no premature removal.

Connections

Check:

- bolts installed;

- temporary bolts replaced where required;

- welds completed;

- connection completeness.

3.3.6 RECORDS / EVIDENCE

Capture:

- member/grid;

- erection date;

- survey/plumb records;

- connection status;

- temporary bracing observations;

- photographs;

- discrepancies;

- final alignment records.

3.3.7 NC / DEFICIENCY

Typical:

- wrong member location;

- reversed member;

- excessive out-of-plumb;

- wrong elevation;

- missing bracing;

- incomplete connection;

- field modification without approval;

- anchor mismatch;

- damaged coating.

3.3.8 CORRECTIVE ACTION — EXAMPLE

Column installed out of plumb beyond project tolerance.

Measure → record → compare criterion → control subsequent framing if required → adjust → re-survey → confirm connection integrity → document acceptance.

3.3.9 VERIFICATION

Confirm:

- alignment;

- plumbness;

- elevation;

- final connections;

- bracing;

- coating repair;

- survey results.

3.3.10 CLOSURE

☐ Correct members
☐ Correct orientation
☐ Alignment accepted
☐ Plumbness accepted
☐ Elevation accepted
☐ Bracing complete
☐ Connections complete
☐ Survey record complete

3.3.11 REPORTING / ANALYSIS

Track:

- recurring anchor conflicts;

- member fit-up problems;

- alignment errors;

- erection-sequence problems;

- fabrication errors discovered during erection.

3.3.12 QUALITY CHECKPOINT

☐ Support accepted
☐ Anchor bolts verified
☐ Member correct
☐ Location correct
☐ Orientation correct
☐ Elevation correct
☐ Plumb/alignment correct
☐ Temporary bracing correct
☐ Connections complete
☐ Survey complete

3.4 BOLTED CONNECTIONS

Quality objective

Ensure that every bolted connection uses the correct approved fasteners, installed in the correct configuration and tightened/inspected according to project requirements.

3.4.1 REQUIREMENTS

Obtain:

- connection drawings;

- structural specifications;

- bolt type/grade;

- approved shop drawings;

- installation method;

- tightening requirements;

- inspection/testing requirements;

- PIE/PRIE;

- applicable referenced standards.

3.4.2 PLANNING

Know:

- which connections require inspection;

- bolt type;

- pretension requirements;

- installation method;

- lot identification where required;

- inspection method;

- hold/witness points.

3.4.3 DOCUMENT CONTROL

Verify current:

- connection detail;

- bolt grade;

- washer/nut requirements;

- tightening method;

- inspection criteria.

3.4.4 MATERIAL CONTROL

Check:

- bolt diameter;

- length;

- grade;

- nuts;

- washers;

- manufacturer/lot identification where required;

- condition;

- storage.

Prevent:

- mixed bolt grades;

- contaminated threads;

- damaged fasteners;

- untraceable lots.

3.4.5 INSPECTION / TESTING

Check:

Installation

- correct bolts;

- full bolt count;

- correct orientation where applicable;

- washers installed as required;

- threads engaged;

- holes aligned;

- faying surfaces acceptable where relevant.

Tightening

Verify approved method such as project-specific:

- turn-of-nut;

- calibrated wrench;

- tension-control bolts;

- direct-tension indicators;

- other specified method.

Do not assume method.

Inspection/testing

Follow specified method/frequency.

3.4.6 RECORDS / EVIDENCE

Retain:

- connection ID;

- bolt type;

- lot records where required;

- installation method;

- inspection result;

- torque/calibration records where applicable;

- photos;

- deficiency/reinspection records.

3.4.7 NC / DEFICIENCY

Common:

- wrong bolt grade;

- missing bolt;

- missing washer;

- insufficient tightening;

- damaged threads;

- unapproved substitution;

- mixed lots;

- incomplete connection.

3.4.8 CORRECTIVE ACTION — EXAMPLE

Inspection identifies several bolts not fully tensioned.

Identify exact connection → mark affected bolts → notify → retighten/reinstall according to approved method → reinspect → document → close.

3.4.9 VERIFICATION

Reinspect:

- bolt count;

- bolt condition;

- installation;

- tightening;

- connection completeness.

3.4.10 CLOSURE

☐ Correct fasteners
☐ Complete bolt count
☐ Installation correct
☐ Tightening accepted
☐ Inspection records complete
☐ Connection released

3.4.11 REPORTING / ANALYSIS

Look for:

- recurring under-tightening;

- wrong bolt grades;

- repeated incomplete connections;

- storage/traceability issues.

3.4.12 QUALITY CHECKPOINT

☐ Detail correct
☐ Bolt grade correct
☐ Diameter/length correct
☐ Nuts/washers correct
☐ Bolt count complete
☐ Tightening method correct
☐ Inspection complete
☐ Deficiencies closed

3.5 WELDING

Quality objective

Ensure welded structural connections are produced using approved procedures by qualified personnel under acceptable conditions, and that completed welds satisfy required inspection/testing criteria.

3.5.1 REQUIREMENTS

🔵 Obtain:

- approved shop drawings;

- weld symbols/details;

- welding specifications;

- approved WPS;

- welder qualifications;

- consumable requirements;

- preheat/interpass requirements;

- environmental limitations;

- NDT requirements;

- repair procedures;

- PIE/PRIE;

- referenced welding standards.

3.5.2 PLANNING

Before welding:

- identify connection/weld;

- confirm WPS;

- confirm welder qualification;

- confirm base material;

- confirm consumables;

- determine inspection/NDT;

- coordinate third-party inspector if required;

- verify weather/environmental protection.

3.5.3 DOCUMENT CONTROL

Verify:

☐ current WPS
☐ welder qualification valid/applicable
☐ latest drawing
☐ weld size/type correct
☐ NDT requirements known
☐ repair procedure available if needed

3.5.4 MATERIAL CONTROL

Verify:

- base material;

- electrodes/wire;

- consumable classification;

- storage;

- drying/handling requirements;

- shielding gases where applicable.

3.5.5 INSPECTION / TESTING

Before welding

Check:

- joint preparation;

- bevel;

- root opening;

- cleanliness;

- fit-up;

- alignment;

- tack welds;

- preheat requirement;

- environmental protection.

During welding

Observe where applicable:

- WPS followed;

- preheat/interpass;

- sequence;

- consumable control;

- arc strikes;

- distortion control.

After welding — visual

Check:

- weld size;

- length;

- profile;

- continuity;

- undercut;

- overlap;

- porosity;

- cracks;

- incomplete fusion indicators;

- spatter;

- arc strikes;

- final geometry.

NDT

Where required:

- VT;

- MT;

- PT;

- UT;

- RT;

depending on project requirements.

3.5.6 RECORDS / EVIDENCE

Retain:

- weld ID;

- welder ID;

- WPS;

- joint/location;

- visual-inspection result;

- NDT report;

- consumable records where required;

- temperature/preheat records where required;

- repair/reinspection records.

3.5.7 NC / DEFICIENCY

Typical:

- unqualified welder;

- wrong WPS;

- inadequate joint prep;

- crack;

- excessive undercut;

- porosity;

- incomplete weld;

- failed NDT;

- unapproved repair;

- welding outside required environmental conditions.

3.5.8 CORRECTIVE ACTION — EXAMPLE

UT identifies unacceptable discontinuity.

Locate weld → identify report → control affected connection → obtain approved repair method → remove defective area → reweld under approved WPS → repeat required NDT → document closure.

3.5.9 VERIFICATION

Confirm:

- defect removed;

- approved repair used;

- qualified welder;

- visual acceptable;

- NDT passed;

- coating restored afterward where required.

3.5.10 CLOSURE

☐ WPS valid
☐ Welder qualified
☐ Joint accepted
☐ Visual accepted
☐ NDT accepted
☐ Repairs closed
☐ Records complete

3.5.11 REPORTING / ANALYSIS

Trend:

- repeated weld defects by type;

- recurring welder issues;

- fit-up problems;

- environmental problems;

- repeated NDT failures;

- fabrication/erection coordination problems.

3.5.12 QUALITY CHECKPOINT

☐ Drawing/WPS correct
☐ Welder qualified
☐ Joint prep correct
☐ Materials/consumables correct
☐ Conditions acceptable
☐ Weld complete
☐ Visual passed
☐ NDT passed where required
☐ Repairs closed

3.6 STEEL PROTECTION

This includes:

galvanizing → protective coatings → fireproofing → repair of damaged protection

Quality objective

Ensure structural steel receives and retains the specified protection against corrosion, fire exposure and environmental conditions throughout delivery, erection and completion.

3.6.1 REQUIREMENTS

Obtain:

- steel/coating specifications;

- galvanizing requirements;

- paint/coating system;

- fireproofing system;

- approved product sheets;

- surface-preparation requirements;

- dry-film thickness requirements;

- environmental limits;

- repair procedures;

- PIE/PRIE.

3.6.2 PLANNING

Identify:

- factory vs field-applied coating;

- surfaces requiring repair after erection;

- areas inaccessible later;

- connection areas;

- weld repair zones;

- fireproofing sequence;

- environmental monitoring.

3.6.3 DOCUMENT CONTROL

Verify:

☐ approved product
☐ correct system/layers
☐ current manufacturer instructions
☐ required surface prep
☐ thickness criteria
☐ repair procedure

3.6.4 MATERIAL CONTROL

Check:

- coating product;

- batch;

- shelf life;

- storage;

- compatibility;

- fireproofing material;

- primer compatibility;

- repair material.

3.6.5 INSPECTION / TESTING

Galvanizing

Inspect:

- coverage;

- damage;

- exposed steel;

- drips/defects where relevant;

- repaired areas.

Protective coatings

Check:

- surface preparation;

- cleanliness;

- environmental conditions;

- primer/intermediate/topcoat;

- coverage;

- dry-film thickness where required;

- runs/sags;

- holidays/missed areas.

Fireproofing

Check:

- substrate;

- primer compatibility;

- thickness;

- density where required;

- adhesion;

- continuity;

- damage;

- interfaces.

3.6.6 RECORDS / EVIDENCE

Capture:

- product/batch;

- surface prep;

- ambient conditions;

- DFT readings;

- fireproofing thickness;

- inspection records;

- photos;

- repair records.

3.6.7 NC / DEFICIENCY

Common:

- coating damage;

- inadequate thickness;

- poor surface prep;

- missed areas;

- incompatible coating;

- fireproofing too thin;

- delamination;

- damage after installation.

3.6.8 CORRECTIVE ACTION — EXAMPLE

Steel connection coating damaged during erection.

Mark affected area → confirm repair system → prepare surface → apply approved repair coating → verify thickness/coverage → photograph → close.

3.6.9 VERIFICATION

Confirm:

- damaged area fully treated;

- required layers applied;

- thickness accepted;

- adjacent protection intact.

3.6.10 CLOSURE

☐ Coating complete
☐ Thickness accepted
☐ Fireproofing accepted
☐ Damage repaired
☐ Records complete

3.6.11 REPORTING / ANALYSIS

Track:

- repeated transport/erection damage;

- coating failures;

- repeated thin spots;

- fireproofing damage from later trades.

3.6.12 QUALITY CHECKPOINT

☐ Correct system
☐ Surface prep
☐ Environmental conditions
☐ Coverage
☐ Thickness
☐ Damage repaired
☐ Interfaces complete
☐ Evidence filed

3.7 STRUCTURAL MASONRY

Quality objective

Construct structural masonry using approved units, mortar, reinforcement, grout and anchorage in the correct geometry, alignment and sequence, with required testing and full traceability.

3.7.1 REQUIREMENTS

Obtain:

- masonry structural drawings;

- wall layouts;

- sections;

- reinforcement details;

- lintel details;

- bond-beam details;

- control-joint locations;

- approved shop drawings;

- masonry specifications;

- unit approvals;

- mortar requirements;

- grout requirements;

- reinforcement/anchors;

- testing requirements;

- PIE/PRIE.

3.7.2 PLANNING

Before work:

- identify wall type;

- structural/nonstructural interface;

- wall height/lifts;

- reinforcement;

- grout sequence;

- embeds/openings;

- lintels;

- MEP penetrations;

- testing;

- cold/hot weather requirements;

- inspection before cells are concealed/grouted.

3.7.3 DOCUMENT CONTROL

Verify:

☐ correct wall layout
☐ current details
☐ reinforcement schedule
☐ lintel details
☐ control joints
☐ embed/opening changes
☐ current material approvals

3.7.4 MATERIAL CONTROL

Verify:

Units

- type;

- strength/class;

- dimensions;

- condition;

- manufacturer;

- certificates/tests.

Mortar

- type;

- ingredients/prepackaged product;

- batching;

- water;

- mixing time;

- use time.

Grout

- approved mix;

- consistency;

- delivery/batch information;

- testing.

Reinforcement

- size;

- grade;

- condition.

Anchors/ties

- type;

- spacing;

- approval.

3.7.5 INSPECTION / TESTING

Blocks

Check:

- correct type;

- undamaged;

- clean;

- correct orientation.

Mortar

Check:

- correct type;

- consistent mixing;

- joints full;

- joint thickness;

- tooling where applicable.

Geometry

- line;

- level;

- plumb;

- wall thickness;

- openings.

Reinforcement

- vertical bars;

- horizontal reinforcement;

- spacing;

- laps;

- anchorage;

- positioning.

Grout

Before grout:

- cells clean;

- reinforcement correct;

- openings/provisions correct.

During grout:

- approved material;

- placement;

- lift height;

- consolidation;

- testing where required.

Anchors

Check:

- type;

- spacing;

- embedment;

- connection.

Lintels

Verify:

- correct unit/type;

- bearing;

- reinforcement;

- grout;

- elevation.

Control joints

Verify:

- location;

- continuity;

- correct detailing.

3.7.6 RECORDS / EVIDENCE

Capture:

- wall/grid;

- material approvals;

- delivery info;

- unit/mortar/grout tests;

- reinforcement photos before grout;

- anchor/lintel photos;

- grout placement records;

- inspection forms;

- deficiency/repair records.

3.7.7 NC / DEFICIENCY

Typical:

- wrong block type;

- cracked/damaged units;

- wrong mortar;

- poor joints;

- out-of-plumb wall;

- missing rebar;

- wrong bar spacing;

- ungrouted cells;

- incorrect lintel;

- missing anchors;

- wrong control-joint location;

- grout voids.

3.7.8 CORRECTIVE ACTION — EXAMPLE

Inspection before grout finds missing vertical reinforcement in several cells.

Control grouting → identify wall/grid/cells → compare reinforcement drawing → install correct bars/anchorage → reinspect → photograph → release grout.

If discovered after grouting, escalate for engineered disposition.

3.7.9 VERIFICATION

Confirm:

- corrected units/rebar;

- wall alignment;

- grout complete;

- anchors/lintels;

- test results;

- repaired areas.

3.7.10 CLOSURE

☐ Units correct
☐ Mortar acceptable
☐ Alignment/plumb accepted
☐ Reinforcement accepted
☐ Grout accepted
☐ Anchors complete
☐ Lintels complete
☐ Control joints correct
☐ Testing accepted
☐ Records complete

3.7.11 REPORTING / ANALYSIS

Trend:

- recurring plumbness problems;

- missing reinforcement;

- grout issues;

- mortar inconsistencies;

- repeated damaged blocks;

- recurring anchor omissions.

3.7.12 QUALITY CHECKPOINT

☐ Correct units
☐ Correct mortar
☐ Wall location
☐ Line/level/plumb
☐ Reinforcement
☐ Anchors
☐ Lintels
☐ Control joints
☐ Grout
☐ Testing
☐ Pre-concealment photos
☐ Final acceptance

3.8 PRECAST ELEMENTS — IF APPLICABLE

Quality objective

Ensure precast elements arrive with approved fabrication documentation, are undamaged and traceable, and are erected in the correct location/alignment with compliant connections, grouting and repairs.

3.8.1 REQUIREMENTS

Obtain:

- approved precast shop drawings;

- erection drawings;

- fabrication requirements;

- member schedules;

- connection details;

- embeds;

- tolerances;

- grout specifications;

- weld/bolt details;

- lifting requirements;

- fabrication inspection records;

- concrete test records;

- PIE/PRIE.

3.8.2 PLANNING

Before delivery/erection:

- identify elements;

- delivery sequence;

- storage;

- crane sequence;

- bearing/support readiness;

- embeds/anchors;

- connection materials;

- grout;

- erection survey;

- inspection requirements.

3.8.3 DOCUMENT CONTROL

Verify:

☐ approved fabrication drawings
☐ approved erection drawings
☐ member IDs
☐ connection details
☐ latest revisions
☐ required fabrication records

3.8.4 MATERIAL CONTROL

On receipt check:

- member ID;

- dimensions;

- certificates;

- fabrication records;

- concrete strength evidence;

- surface condition;

- cracks;

- chips;

- spalls;

- exposed reinforcement;

- damaged embeds;

- connection plates;

- bearing pads;

- grout/materials.

3.8.5 INSPECTION / TESTING

Receiving

- member ID;

- damage;

- dimensions where relevant;

- embed condition;

- storage support.

Erection

Check:

- correct member;

- location;

- orientation;

- elevation;

- bearing;

- alignment;

- plumbness;

- temporary stability.

Connections

Check:

- bolts;

- welds;

- plates;

- embeds;

- bearing pads;

- joint width.

Grouting

Check:

- approved grout;

- preparation;

- placement;

- consolidation;

- cure.

3.8.6 RECORDS / EVIDENCE

Retain:

- member ID;

- fabrication records;

- delivery record;

- receiving photos;

- damage record;

- erection survey;

- connection inspection;

- grout records;

- repair evidence.

3.8.7 NC / DEFICIENCY

Common:

- wrong member;

- damage;

- cracked element;

- missing embed;

- wrong bearing;

- alignment issue;

- incomplete connection;

- grout void;

- unapproved field modification.

3.8.8 CORRECTIVE ACTION — EXAMPLE

Precast panel arrives with corner spall.

Identify member → photograph → determine extent → control installation if necessary → obtain approved repair disposition → repair or replace → reinspect → document → release.

3.8.9 VERIFICATION

Confirm:

- repaired damage;

- member location;

- alignment;

- connections;

- grout;

- final survey;

- repair acceptance.

3.8.10 CLOSURE

☐ Fabrication records complete
☐ Member accepted
☐ Erection accepted
☐ Alignment accepted
☐ Connections complete
☐ Grout complete
☐ Repairs closed
☐ Records complete

3.8.11 REPORTING / ANALYSIS

Track:

- repeated transport damage;

- recurring embed mismatch;

- connection problems;

- grout defects;

- fabrication dimensional errors.

3.8.12 QUALITY CHECKPOINT

☐ Correct member
☐ Documentation
☐ No unresolved damage
☐ Correct location/orientation
☐ Bearing correct
☐ Alignment/plumbness
☐ Connections
☐ Grout
☐ Survey
☐ Repair closure

SUPERSTRUCTURE MASTER QUALITY GATE

Before considering a structural zone complete:

Concrete

☐ Formwork accepted
☐ Reinforcement accepted
☐ Embeds accepted
☐ Pre-pour cleared
☐ Concrete tested
☐ Curing complete
☐ Strength results accepted
☐ Repairs closed

Structural steel

☐ Materials traceable
☐ Certifications complete
☐ Members correct
☐ Alignment/plumbness accepted
☐ Bolts accepted
☐ Welds accepted
☐ NDT complete
☐ Protection restored

Masonry

☐ Units/materials accepted
☐ Geometry accepted
☐ Reinforcement accepted
☐ Grout accepted
☐ Lintels/anchors complete
☐ Tests accepted

Precast

☐ Fabrication documentation
☐ Receiving accepted
☐ Erection accepted
☐ Connections/grout accepted
☐ Repairs closed

Interfaces

☐ Structural embeds correct
☐ MEP openings correct
☐ Equipment/anchor interfaces correct
☐ Envelope interfaces coordinated
☐ No unresolved dimensional conflicts

Documentation

☐ Inspection records
☐ Test results
☐ Photos
☐ Survey records
☐ Material certificates
☐ NCR/deficiency closure
☐ Responsable qualité updated

The principle remains:

A structural element is not “quality complete” merely because it is physically standing.

It is complete when:

correct requirement + approved material + correct installation + required inspection/testing + objective evidence + resolved deviations + verified closure

all line up.

Absolutely. Building envelope deserves one of the deepest modules in the whole system because envelope defects are often:

- concealed;

- repetitive across large areas;

- expensive to repair later;

- difficult to diagnose once the building is closed;

- directly tied to water infiltration, air leakage, condensation, heat loss, mold, corrosion, and occupant complaints.

The quality objective for the envelope is:

Create a continuous, durable, coordinated environmental separation between exterior and interior conditions, with controlled water, air, vapour and heat flow across walls, openings, penetrations and transitions.

And the key word is continuity.

A wall can have excellent insulation, excellent membrane, excellent flashing, and still fail if those systems are not properly connected at:

windows → doors → roof → foundation → penetrations → corners → joints → structural interfaces.

So our envelope QC system must inspect not only components, but also interfaces.

4. BUILDING ENVELOPE

4.1 EXTERIOR WALL ASSEMBLIES

This is the umbrella workflow that coordinates all envelope layers.

Quality objective

Ensure the complete exterior wall assembly is built in the correct sequence, with compatible approved materials, continuous control layers, correct drainage and ventilation paths, and proper integration at openings and interfaces.

A typical exterior wall may include:

interior finish → vapour control → framing → insulation → sheathing → air barrier → exterior insulation → drainage cavity → flashing → cladding/masonry

But the actual Hochelaga assembly must come from the approved project documents.

4.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- architectural wall sections;

- enlarged wall details;

- envelope details;

- structural drawings;

- exterior elevations;

- window/door details;

- roof-wall details;

- foundation-wall details;

- approved shop drawings;

- approved mock-up details where applicable;

- envelope specifications;

- air barrier specifications;

- vapour barrier specifications;

- insulation specifications;

- cladding/masonry specifications;

- sealant specifications;

- firestopping/interface requirements;

- manufacturer installation instructions;

- approved technical sheets;

- Plan Qualité;

- PIE/PRIE;

- technical directives;

- QMT/RFI responses;

- approved substitutions.

Extract

For each wall type:

- wall assembly designation;

- layer sequence;

- material type;

- thickness;

- fastening method;

- continuity requirements;

- cavity dimension;

- drainage path;

- flashing;

- air barrier location;

- vapour barrier location;

- insulation location;

- penetration detailing;

- opening detailing;

- transition detailing;

- sealant requirements;

- fire/life-safety interfaces.

4.1.2 PLANNING

Before wall construction:

- identify wall type by elevation/zone;

- understand sequence of trades;

- identify pre-concealment inspections;

- identify required mock-ups;

- identify manufacturer inspections if required;

- identify testing;

- identify areas where one trade hands work to another.

Build the layer sequence mentally

For each wall:

What layer is being installed now? What layer comes next? What becomes hidden?

That is critical.

For example:

sheathing installed → air barrier installed → exterior insulation installed

Once insulation covers the air barrier, a large portion of the membrane becomes difficult to inspect.

So your system should flag:

PRE-CONCEALMENT QUALITY GATE — AIR BARRIER BEFORE INSULATION/CLADDING

4.1.3 DOCUMENT CONTROL

Verify:

☐ correct wall type
☐ latest architectural detail
☐ latest shop drawing
☐ current manufacturer details
☐ approved substitutions incorporated
☐ technical changes incorporated
☐ current window/door interface details
☐ current roof/foundation transition details

Common risk

Multiple details may apply to the same physical area.

Example:

A window sill may involve:

- wall section;

- window shop drawing;

- air barrier detail;

- flashing detail;

- sealant detail;

- structural opening;

- insulation detail.

Your QC task is to ensure those documents are coordinated, not read independently.

4.1.4 MATERIAL CONTROL

Verify:

- all layers approved;

- compatibility between adjacent products;

- manufacturer;

- thickness;

- batch/product ID where required;

- storage;

- moisture exposure;

- damaged materials;

- shelf life for liquid membranes/sealants;

- substrate requirements.

Particularly verify compatibility between:

air barrier + primer + flashing membrane + sealant + insulation adhesive

because incompatible materials can undermine an otherwise correct detail.

4.1.5 INSPECTION / TESTING

Inspect assembly progressively:

Before enclosure

- framing;

- substrate;

- sheathing;

- penetrations;

- openings.

Control layers

- air barrier;

- vapour barrier;

- insulation;

- flashing.

Exterior finish

- cavity;

- anchors;

- cladding/masonry;

- sealants.

Interfaces

- window perimeter;

- door perimeter;

- wall-to-roof;

- wall-to-foundation;

- wall-to-structure;

- penetrations;

- corners;

- movement joints.

4.1.6 RECORDS / EVIDENCE

Strong envelope records include:

- wall type/zone;

- elevation/grid;

- date;

- installed layer;

- approved detail reference;

- photos before concealment;

- product batch/approval where required;

- inspection checklist;

- test results;

- deficiencies;

- repairs;

- final condition.

Envelope photo strategy

Use:

overall elevation → specific bay/opening → close-up of detail

because envelope issues are highly location-dependent.

4.1.7 NC / DEFICIENCY

Common assembly-level issues:

- wrong layer sequence;

- incompatible materials;

- discontinuous air barrier;

- missing insulation;

- blocked drainage cavity;

- incorrect flashing;

- missing weeps;

- penetrations not sealed;

- cladding installed before membrane acceptance;

- revised detail not incorporated.

4.1.8 CORRECTIVE ACTION — EXAMPLE

Scenario

Exterior insulation has already started covering an area where air barrier seams have not been inspected.

System response:

Identify area → stop local concealment → expose as required → inspect membrane → document deficiencies → repair → reinspect → photograph → release insulation installation.

The objective is not to create conflict with the trade.

It is to prevent lost inspection opportunity.

4.1.9 VERIFICATION

Verify:

- repaired layer;

- continuity restored;

- compatibility maintained;

- downstream layer not damaged;

- required testing completed;

- records complete.

4.1.10 CLOSURE

☐ correct wall assembly
☐ all layers approved
☐ control layers continuous
☐ openings integrated
☐ penetrations sealed
☐ drainage maintained
☐ cladding/masonry complete
☐ sealants complete
☐ tests accepted
☐ deficiencies closed

4.1.11 REPORTING / ANALYSIS

Track:

- recurring membrane damage;

- recurring window interface defects;

- repeated missing insulation;

- blocked cavities;

- inconsistent flashing;

- repeated sealant failures;

- trade coordination problems.

4.1.12 QUALITY CHECKPOINT

☐ Correct wall type
☐ Correct sequence
☐ Materials approved
☐ Air barrier continuous
☐ Vapour barrier continuous
☐ Insulation continuous
☐ Drainage path intact
☐ Openings detailed
☐ Penetrations sealed
☐ Flashing complete
☐ Cladding/masonry accepted
☐ Sealants accepted
☐ Pre-concealment photos complete

4.2 AIR BARRIER

This is one of the highest-priority envelope QC modules.

Quality objective

Create a continuous, durable, properly bonded and sealed air-control layer across the entire envelope, including joints, penetrations, openings and transitions.

The biggest air-barrier failures are rarely in the middle of a large flat membrane.

They occur at:

edges → corners → penetrations → openings → transitions → structural interfaces.

4.2.1 REQUIREMENTS

🔵 Obtain:

- architectural envelope drawings;

- air barrier details;

- wall sections;

- window/door details;

- roof transitions;

- foundation transitions;

- penetration details;

- approved product data;

- manufacturer instructions;

- primer requirements;

- substrate requirements;

- temperature/weather limitations;

- adhesion requirements;

- lap requirements;

- approved repair methods;

- testing requirements;

- PIE/PRIE.

4.2.2 PLANNING

Before installation:

- determine air barrier type;

- identify substrate;

- identify sequence;

- identify transitions;

- identify penetrations;

- identify openings;

- determine required mock-up/testing;

- inspect before concealment.

Pre-work walkdown

Walk the area and ask:

- Are there penetrations not yet coordinated?

- Are substrates ready?

- Are openings complete?

- Are there wet/dirty/damaged surfaces?

- Will another trade penetrate the membrane tomorrow?

4.2.3 DOCUMENT CONTROL

Verify:

☐ latest air barrier details
☐ approved product
☐ approved primer
☐ approved flashing membrane
☐ current window transition detail
☐ current roof/foundation transition detail
☐ manufacturer instructions current

4.2.4 MATERIAL CONTROL

Verify:

- correct membrane;

- primer;

- transition membrane;

- liquid flashing;

- sealant;

- accessories;

- shelf life;

- storage temperature;

- damaged rolls/containers;

- compatibility.

4.2.5 INSPECTION / TESTING

A. SUBSTRATE

Check:

- clean;

- dry as required;

- smooth;

- sound;

- free of dust/oil;

- voids repaired;

- joints prepared;

- fasteners flush;

- acceptable temperature.

B. PRODUCT

Verify correct product installed in correct location.

C. CONTINUITY

Inspect membrane as a continuous plane.

Ask:

Can air bypass this membrane anywhere?

D. SEAMS / LAPS

Check:

- correct overlap;

- fully bonded;

- no fishmouths;

- wrinkles controlled;

- seams rolled where required;

- no open edges.

E. TRANSITIONS

Critical locations:

- wall-to-foundation;

- wall-to-roof;

- wall-to-window;

- wall-to-door;

- material changes;

- structural frame interfaces.

F. PENETRATIONS

Check:

- pipes;

- conduits;

- ducts;

- anchors;

- brackets;

- structural members.

Verify proper sealing around each.

G. OPENINGS

For windows/doors:

- membrane turned into opening as required;

- sill/head/jamb treatment;

- corners fully sealed;

- compatible transition materials.

H. REPAIRS

Inspect:

- punctures;

- tears;

- fastener damage;

- construction damage;

- patch size;

- lap/adhesion.

4.2.6 RECORDS / EVIDENCE

Capture:

- elevation/grid;

- membrane product;

- batch where required;

- substrate condition;

- weather/temp where required;

- seam photos;

- transition photos;

- penetrations;

- openings;

- repairs;

- test reports;

- pre-concealment release.

4.2.7 NC / DEFICIENCY

Common:

- membrane installed over wet substrate;

- inadequate adhesion;

- insufficient lap;

- open seam;

- tear/puncture;

- missing transition;

- unsealed penetration;

- wrinkle/fishmouth;

- incompatible sealant;

- premature concealment.

4.2.8 CORRECTIVE ACTION — EXAMPLE

Scenario

Membrane around conduit penetration is cut irregularly and not sealed.

Identify → photograph → stop concealment → verify approved penetration detail → install compatible patch/liquid flashing/sealant as specified → reinspect → photograph → release.

4.2.9 VERIFICATION

Confirm:

- continuity;

- adhesion;

- patch dimensions;

- penetration fully sealed;

- no new damage;

- required testing passes.

4.2.10 CLOSURE

☐ substrate accepted
☐ membrane correct
☐ seams accepted
☐ transitions complete
☐ penetrations sealed
☐ openings integrated
☐ repairs complete
☐ testing accepted
☐ pre-concealment record complete

4.2.11 REPORTING / ANALYSIS

Track:

- repeated punctures by later trades;

- recurring poor adhesion;

- transition failures;

- penetrations installed after membrane;

- recurring window-interface issues.

4.2.12 AIR BARRIER QUALITY CHECKPOINT

BEFORE

☐ Substrate ready
☐ Product approved
☐ Weather/temp acceptable
☐ Details available

INSTALLATION

☐ Continuous membrane
☐ Laps correct
☐ Seams bonded
☐ Corners sealed
☐ Transitions complete
☐ Penetrations sealed
☐ Openings treated

PRE-CONCEALMENT

☐ Damage repaired
☐ Photos complete
☐ Testing complete
☐ Area released

4.3 VAPOUR BARRIER

Quality objective

Maintain the intended vapour-control layer continuously and in the correct location within the wall/roof assembly to limit moisture migration and condensation risk.

The correct location and permeability depend on the designed wall assembly.

Do not assume “vapour barrier always goes on the warm side” without checking project design.

4.3.1 REQUIREMENTS

Obtain:

- wall sections;

- vapour-control details;

- roof details;

- product data;

- manufacturer instructions;

- continuity details;

- openings/penetration details;

- specifications;

- PIE/PRIE.

Extract:

- product;

- vapour permeance requirement;

- location in assembly;

- lap requirement;

- sealing method;

- penetrations;

- interfaces;

- repair method.

4.3.2 PLANNING

Identify:

- areas becoming concealed by drywall/interior finish;

- service penetrations;

- electrical boxes;

- framing interfaces;

- ceiling/wall interfaces;

- roof transitions.

4.3.3 DOCUMENT CONTROL

Verify:

☐ correct wall/roof type
☐ correct membrane
☐ correct location
☐ current details
☐ technical changes incorporated

4.3.4 MATERIAL CONTROL

Verify:

- approved membrane;

- tape;

- sealant;

- adhesive;

- accessories;

- compatibility;

- storage;

- damage.

4.3.5 INSPECTION

Check:

- continuity;

- laps;

- seams;

- penetrations;

- boxes/outlets;

- corners;

- edges;

- roof/wall transitions;

- damage;

- fastening;

- sealant continuity.

4.3.6 RECORDS

Capture:

- wall/zone;

- product;

- photos before drywall/concealment;

- seams;

- penetrations;

- repairs;

- inspection checklist.

4.3.7 NC / DEFICIENCY

Common:

- missing membrane;

- reversed/wrong location;

- tears;

- open seams;

- unsealed electrical boxes;

- penetration gaps;

- membrane cut by later trade.

4.3.8 CORRECTIVE ACTION

Example:

Electrical installation punctures vapour membrane.

Document → confirm approved repair → patch/seal → reinspect before drywall closes wall → photo → close.

4.3.9 VERIFICATION

Confirm continuity restored.

4.3.10 CLOSURE

☐ membrane correct
☐ continuity complete
☐ penetrations sealed
☐ repairs complete
☐ photos complete
☐ wall ready for concealment

4.3.11 REPORTING

Trend recurring damage by MEP trades or poor coordination.

4.3.12 QUALITY CHECKPOINT

☐ Correct membrane
☐ Correct location
☐ Seams sealed
☐ Penetrations sealed
☐ Corners complete
☐ Damage repaired
☐ Pre-concealment evidence

4.4 THERMAL INSULATION

Quality objective

Install the correct insulation continuously at the required thickness without gaps, compression, moisture damage or thermal bridges beyond what is permitted by the design.

4.4.1 REQUIREMENTS

Obtain:

- wall sections;

- roof details;

- insulation specifications;

- thermal requirements;

- product approvals;

- fire requirements;

- fastening/adhesive details;

- manufacturer instructions;

- PIE/PRIE.

Extract:

- type;

- thickness;

- density;

- thermal resistance;

- layers;

- joints;

- fasteners;

- continuity;

- interface requirements.

4.4.2 PLANNING

Identify:

- insulation sequence;

- concealed areas;

- penetrations;

- framing;

- corners;

- slab edges;

- structural bridges;

- window/door perimeters.

4.4.3 DOCUMENT CONTROL

Verify:

☐ correct wall type
☐ correct insulation type
☐ correct thickness
☐ current details
☐ technical changes

4.4.4 MATERIAL CONTROL

Check:

- correct product;

- thickness;

- labels;

- condition;

- moisture;

- crushed boards;

- damaged edges;

- storage protection.

4.4.5 INSPECTION

Check:

Product/type

Correct insulation for that location.

Thickness

Verify required total thickness.

Continuity

Look for missing areas.

Fastening

Check spacing/type where specified.

Gaps

Inspect joints/corners.

Compression

Particularly batt insulation.

Over-compression reduces performance.

Moisture/damage

Wet insulation may require replacement depending on product/project requirements.

Interfaces

- window perimeters;

- shelf angles;

- slab edges;

- penetrations;

- equipment supports.

4.4.6 RECORDS

Capture:

- wall/zone;

- product;

- thickness;

- photos before concealment;

- fastening;

- corners;

- penetrations;

- defects/repairs.

4.4.7 NC / DEFICIENCY

Common:

- wrong thickness;

- wrong product;

- missing insulation;

- gaps;

- compressed insulation;

- wet material;

- damaged boards;

- loose attachment.

4.4.8 CORRECTIVE ACTION — EXAMPLE

Board insulation has multiple large gaps around steel brackets.

Identify → verify detail → cut/fill insulation correctly → seal joints if required → reinspect → photograph before cladding.

4.4.9 VERIFICATION

Confirm:

- continuity;

- thickness;

- fastening;

- dry/undamaged condition.

4.4.10 CLOSURE

☐ correct type
☐ correct thickness
☐ continuous
☐ fastening complete
☐ gaps repaired
☐ moisture issues resolved
☐ evidence complete

4.4.11 REPORTING / ANALYSIS

Track:

- recurring gaps;

- recurring wet material;

- poor cutting around penetrations;

- fastening problems;

- coordination-related thermal bridging.

4.4.12 QUALITY CHECKPOINT

☐ Product
☐ Thickness
☐ Continuity
☐ Fasteners
☐ Joints
☐ Penetrations
☐ No compression
☐ No wet/damaged material
☐ Pre-concealment photos

4.5 EXTERIOR SHEATHING

Quality objective

Provide a flat, properly fastened, continuous substrate suitable for the envelope systems installed over it.

4.5.1 REQUIREMENTS

Obtain:

- wall sections;

- sheathing specifications;

- framing details;

- fastener requirements;

- joint requirements;

- fire/moisture requirements;

- approved product data;

- PIE/PRIE.

4.5.2 PLANNING

Before installation:

- verify framing complete;

- openings coordinated;

- backing available;

- penetration locations known;

- air barrier substrate requirements understood.

4.5.3 DOCUMENT CONTROL

Verify correct:

- product;

- thickness;

- orientation;

- fastener pattern;

- joint detail.

4.5.4 MATERIAL CONTROL

Check:

- product/type;

- thickness;

- damaged sheets;

- moisture exposure;

- edge damage;

- storage.

4.5.5 INSPECTION

Check:

- orientation;

- joints;

- fastener spacing;

- edge support;

- flatness;

- gaps;

- damaged areas;

- openings;

- penetrations;

- continuity;

- surface suitability for membrane.

4.5.6 RECORDS

Photos of:

- representative wall areas;

- joints;

- openings;

- defects;

- corrections.

4.5.7 NC / DEFICIENCY

Common:

- wrong sheathing type;

- wrong thickness;

- insufficient fasteners;

- damaged panels;

- unsupported edges;

- excessive gaps;

- wet/deteriorated sheathing.

4.5.8 CORRECTIVE ACTION

Replace/repair according to approved requirements before membrane installation.

4.5.9 VERIFICATION

Reinspect repaired substrate.

4.5.10 CLOSURE

☐ product correct
☐ thickness correct
☐ fastening accepted
☐ joints acceptable
☐ substrate sound
☐ ready for membrane

4.5.11 REPORTING

Track repetitive installation defects that may affect membrane quality.

4.5.12 QUALITY CHECKPOINT

☐ Framing ready
☐ Correct sheathing
☐ Correct thickness
☐ Fasteners correct
☐ Joints correct
☐ Openings correct
☐ Surface acceptable
☐ Damage resolved

4.6 EXTERIOR MASONRY / VENEER

Quality objective

Construct a durable, aligned exterior masonry veneer with approved materials, correct anchorage, functioning drainage cavity, proper flashing/weeps, and controlled joints.

4.6.1 REQUIREMENTS

Obtain:

- elevations;

- wall sections;

- masonry details;

- masonry specifications;

- brick/block approvals;

- mortar requirements;

- anchors/ties;

- shelf-angle details;

- flashing;

- weeps;

- control/movement joints;

- lintels;

- sealants;

- cleaning requirements;

- mock-up requirements;

- PIE/PRIE.

4.6.2 PLANNING

Plan:

- mock-up approval;

- material delivery;

- wall sequence;

- flashing installation;

- anchors;

- cavity cleanliness;

- openings;

- shelf angles;

- control joints;

- cold/hot weather measures.

4.6.3 DOCUMENT CONTROL

Verify:

☐ elevation pattern
☐ approved brick/block
☐ mortar type
☐ anchor spacing
☐ flashing details
☐ weep locations
☐ joint locations
☐ opening details

4.6.4 MATERIAL CONTROL

Masonry units

Check:

- type;

- colour;

- texture;

- dimensions;

- damage;

- batch consistency where appearance matters.

Mortar

- correct type;

- ingredients;

- batching;

- colour if applicable;

- mixing/use time.

Anchors/ties

- correct system;

- corrosion protection;

- approved type.

Flashing

- approved material;

- compatible accessories.

4.6.5 INSPECTION / TESTING

Materials

Correct units/mortar.

Mortar joints

Check:

- full bedding;

- joint thickness;

- tooling;

- consistency.

Anchors/ties

Check:

- type;

- spacing;

- attachment;

- embedment;

- orientation.

Air space/cavity

Inspect:

- required clear space;

- mortar droppings;

- blocked drainage.

Flashing

Critical at:

- base;

- shelf angles;

- window heads;

- door heads;

- wall transitions.

Check:

- continuity;

- slope;

- end dams where required;

- penetrations;

- termination.

Weep holes

Check:

- location;

- spacing;

- unobstructed condition.

Joints

Check:

- control/expansion joints;

- sealant readiness;

- continuity.

Alignment

- line;

- level;

- plumb;

- coursing.

Cleaning

Verify approved method and avoid damage/staining.

4.6.6 RECORDS

Capture:

- elevation/zone;

- material approvals;

- flashing before concealment;

- anchors/ties;

- cavity;

- weeps;

- joints;

- alignment;

- defects;

- repairs.

4.6.7 NC / DEFICIENCY

Common:

- missing anchors;

- excessive anchor spacing;

- blocked cavity;

- missing flashing;

- missing end dam;

- blocked weep;

- poor joint tooling;

- out-of-plumb veneer;

- mismatched units;

- incorrect movement-joint location.

4.6.8 CORRECTIVE ACTION — EXAMPLE

Flashing above window has no end dam.

Because masonry above may soon conceal it:

identify → stop local progression → verify approved detail → install end dam correctly → inspect → photograph → release masonry continuation.

This is exactly where pre-concealment QC saves expensive demolition later.

4.6.9 VERIFICATION

Confirm repaired:

- flashing;

- anchors;

- cavity;

- joints;

- alignment.

4.6.10 CLOSURE

☐ units accepted
☐ mortar accepted
☐ anchors complete
☐ cavity clear
☐ flashing complete
☐ weeps complete
☐ joints complete
☐ alignment accepted
☐ cleaning complete
☐ evidence complete

4.6.11 REPORTING / ANALYSIS

Track:

- repeated cavity blockage;

- missing anchors;

- flashing defects;

- inconsistent mortar;

- recurring alignment issues.

4.6.12 QUALITY CHECKPOINT

☐ Correct units
☐ Correct mortar
☐ Anchors/ties
☐ Air space clear
☐ Flashing continuous
☐ Weeps open
☐ Joints correct
☐ Alignment/plumb
☐ Cleaning acceptable
☐ Pre-concealment evidence

4.7 EXTERIOR CLADDING / PANELS

Quality objective

Install the approved cladding system on a properly aligned substructure, with correct fastening, joints, flashing and envelope interfaces, while maintaining drainage and movement capability.

4.7.1 REQUIREMENTS

Obtain:

- elevations;

- approved shop drawings;

- panel layout;

- support/subframing details;

- fastener details;

- joint details;

- flashing;

- movement joints;

- manufacturer instructions;

- product approvals;

- PIE/PRIE.

4.7.2 PLANNING

Plan:

- substrate acceptance;

- air barrier acceptance;

- insulation acceptance;

- support installation;

- panel sequence;

- openings;

- interfaces;

- replacement access;

- pre-concealment inspection.

4.7.3 DOCUMENT CONTROL

Verify:

☐ correct panel type
☐ current shop drawing
☐ substructure detail
☐ fastener requirements
☐ joint dimension
☐ flashing details
☐ current technical changes

4.7.4 MATERIAL CONTROL

Check:

- panels;

- dimensions;

- finish;

- colour;

- coating;

- damage;

- subframing;

- clips;

- fasteners;

- gaskets;

- flashing.

4.7.5 INSPECTION

Substructure

Check:

- supports;

- spacing;

- alignment;

- anchorage;

- corrosion protection.

Fasteners

Check:

- type;

- quantity;

- location;

- engagement;

- visible damage.

Alignment

- panel lines;

- plumb;

- level;

- plane.

Joints

Check:

- width;

- continuity;

- backer/seal where applicable;

- movement accommodation.

Flashing

Check:

- base;

- heads;

- corners;

- transitions;

- openings.

Interfaces

- windows;

- doors;

- roof;

- masonry;

- penetrations.

4.7.6 RECORDS

Capture:

- elevation/zone;

- subframe inspection;

- representative fastening;

- flashing;

- joints;

- panels;

- damage;

- repairs.

4.7.7 NC / DEFICIENCY

Common:

- wrong panel;

- damaged finish;

- misalignment;

- improper fastener;

- missing clips;

- blocked drainage;

- incorrect joint;

- missing flashing;

- cladding installed over unresolved membrane defect.

4.7.8 CORRECTIVE ACTION

Example:

Panel row visibly misaligned.

Measure → compare approved shop drawing/tolerance → determine affected run → correct subframe/panel installation → reinspect alignment → document.

4.7.9 VERIFICATION

Check:

- alignment;

- fasteners;

- joints;

- flashing;

- repaired finish.

4.7.10 CLOSURE

☐ substructure accepted
☐ panels accepted
☐ fasteners complete
☐ alignment accepted
☐ joints complete
☐ flashing complete
☐ interfaces complete
☐ damage repaired

4.7.11 REPORTING / ANALYSIS

Track:

- recurring alignment issues;

- coating damage;

- missing fasteners;

- poor joint consistency;

- subframe problems.

4.7.12 QUALITY CHECKPOINT

☐ Approved system
☐ Substructure
☐ Fasteners
☐ Alignment
☐ Joints
☐ Flashing
☐ Interfaces
☐ Damage/repair
☐ Final appearance

4.8 WINDOWS / GLAZING

This is another high-risk envelope interface.

Quality objective

Install approved window/glazing assemblies in correctly prepared openings, with proper anchorage, alignment, flashing, air/water sealing and perimeter integration to the surrounding wall system.

4.8.1 REQUIREMENTS

Obtain:

- window schedule;

- elevations;

- opening details;

- approved window shop drawings;

- glazing specifications;

- air/water barrier details;

- sill/head/jamb flashing details;

- sealant specifications;

- anchors;

- manufacturer instructions;

- testing requirements;

- mock-up requirements;

- PIE/PRIE.

4.8.2 PLANNING

Before window installation:

- opening dimensions;

- rough opening condition;

- membrane preparation;

- sill flashing;

- anchor locations;

- perimeter clearance;

- testing schedule;

- pre-install mock-up where required.

4.8.3 DOCUMENT CONTROL

Verify:

☐ correct window type
☐ correct size
☐ current shop drawing
☐ correct opening
☐ approved sealant
☐ approved flashing
☐ current interface detail

4.8.4 MATERIAL CONTROL

Check:

- frame;

- glass;

- coatings/tint;

- hardware;

- gaskets;

- anchors;

- flashing;

- sealant;

- backer rod;

- damage;

- identification.

4.8.5 INSPECTION / TESTING

Opening

Check:

- dimensions;

- square/plumb;

- substrate;

- membrane preparation;

- sill condition.

Window unit

Check:

- correct unit;

- damage;

- orientation.

Anchoring

Check:

- anchor type;

- spacing;

- embedment;

- shims;

- structural fixing.

Alignment

- plumb;

- level;

- square;

- reveal.

Flashing

Inspect:

- sill flashing;

- jamb transitions;

- head flashing;

- end dams;

- drainage path.

Air/water seals

Verify:

- interior/exterior seal strategy;

- continuity;

- compatibility.

Sealants

Check:

- joint geometry;

- backer rod;

- primer;

- adhesion;

- tooling.

Glass

Check:

- correct type;

- damage;

- scratches;

- seals;

- setting.

Testing

Where required:

- water penetration;

- air leakage;

- field testing;

- mock-up testing.

4.8.6 RECORDS

Capture:

- window ID;

- elevation/room;

- opening inspection;

- flashing before concealment;

- anchoring;

- perimeter seals;

- test results;

- defects;

- repairs.

4.8.7 NC / DEFICIENCY

Common:

- wrong window;

- damaged glass;

- opening too large/small;

- poor anchorage;

- out-of-plumb frame;

- missing sill flashing;

- discontinuous air seal;

- incorrect sealant;

- blocked drainage;

- failed water test.

4.8.8 CORRECTIVE ACTION — EXAMPLE

Window fails field water test.

Do not just apply more exterior sealant blindly.

System:

identify leakage location → document test → determine likely pathway → inspect interfaces → obtain approved corrective method → repair specific defect → retest → document pass → close.

4.8.9 VERIFICATION

Confirm:

- repair complete;

- seals continuous;

- drainage maintained;

- window operates;

- retest passes.

4.8.10 CLOSURE

☐ correct unit
☐ opening accepted
☐ anchoring accepted
☐ alignment accepted
☐ flashing complete
☐ air seal complete
☐ water seal complete
☐ glass accepted
☐ testing passed
☐ deficiencies closed

4.8.11 REPORTING / ANALYSIS

Track:

- repeated water-test failures;

- recurring sill detail issue;

- damaged glazing;

- sealant failures;

- anchor issues;

- installer variability.

4.8.12 QUALITY CHECKPOINT

☐ Approved window
☐ Opening correct
☐ Anchors correct
☐ Frame aligned
☐ Sill flashing
☐ Head flashing
☐ Air seal
☐ Water seal
☐ Sealant geometry
☐ Glass condition
☐ Operation
☐ Testing
☐ Closure evidence

4.9 EXTERIOR DOORS

Quality objective

Install exterior door systems that are correctly anchored, aligned, sealed, weather-resistant, secure, operational and compatible with life-safety requirements where applicable.

4.9.1 REQUIREMENTS

Obtain:

- door schedule;

- elevations;

- frame details;

- hardware schedule;

- threshold details;

- weather seal details;

- fire-rating requirements;

- approved shop drawings;

- sealant/flashing details;

- PIE/PRIE.

4.9.2 PLANNING

Before installation:

- verify opening;

- floor elevation;

- threshold;

- frame anchors;

- wall interface;

- hardware;

- security/electrical interface;

- weather seals.

4.9.3 DOCUMENT CONTROL

Verify:

☐ correct door/frame type
☐ correct fire rating where applicable
☐ current hardware schedule
☐ threshold detail
☐ current opening dimensions
☐ approved shop drawings

4.9.4 MATERIAL CONTROL

Check:

- frame;

- door leaf;

- finish;

- hardware;

- hinges;

- closer;

- panic hardware;

- threshold;

- weather seals;

- glazing if present;

- anchors;

- sealants.

4.9.5 INSPECTION

Frames

Check:

- plumb;

- level;

- square;

- anchoring;

- position;

- damage.

Door

Check:

- correct leaf;

- hinge alignment;

- clearances;

- operation.

Hardware

Check:

- correct hardware set;

- fastening;

- operation;

- closer;

- locking;

- panic hardware where applicable.

Weather seals

Check:

- continuity;

- compression;

- corners;

- threshold seal.

Threshold

Check:

- elevation;

- slope;

- seal;

- drainage interface.

Operation

Verify:

- opens/closes smoothly;

- latches;

- locks;

- closer works;

- required clearances.

4.9.6 RECORDS

Capture:

- door ID;

- frame inspection;

- hardware;

- threshold;

- sealants;

- operation test;

- deficiency list.

4.9.7 NC / DEFICIENCY

Common:

- frame out of square;

- poor anchoring;

- wrong hardware;

- door rubs;

- inadequate weather seal;

- threshold leak risk;

- damaged finish;

- fire-rated door mismatch.

4.9.8 CORRECTIVE ACTION

Example:

Door does not latch because frame is twisted.

Measure/frame check → adjust anchors/frame → verify clearances → retest operation → document closure.

4.9.9 VERIFICATION

Recheck:

- alignment;

- hardware;

- seals;

- operation;

- security/life-safety function.

4.9.10 CLOSURE

☐ frame accepted
☐ door accepted
☐ anchors accepted
☐ hardware complete
☐ weather seals complete
☐ threshold accepted
☐ operation accepted
☐ deficiencies closed

4.9.11 REPORTING / ANALYSIS

Track recurring frame/alignment/hardware problems.

4.9.12 QUALITY CHECKPOINT

☐ Correct door/frame
☐ Alignment
☐ Anchoring
☐ Hardware
☐ Weather seal
☐ Threshold
☐ Sealants
☐ Operation
☐ Fire/life-safety interface where applicable

4.10 SEALANTS

Sealants look simple but are frequently a major source of envelope failure.

Quality objective

Create durable, properly dimensioned, compatible, well-adhered flexible joints that accommodate movement while maintaining air/water continuity.

4.10.1 REQUIREMENTS

Obtain:

- sealant specifications;

- approved products;

- joint details;

- manufacturer instructions;

- compatibility testing;

- adhesion testing requirements;

- primer requirements;

- backer rod;

- joint dimensions;

- environmental limitations;

- colour/finish requirements;

- PIE/PRIE.

4.10.2 PLANNING

Before sealing:

- substrate must be complete;

- joint geometry verified;

- incompatible materials identified;

- temperature/weather considered;

- access available;

- mock-up/adhesion testing performed if required.

4.10.3 DOCUMENT CONTROL

Verify:

☐ correct sealant for joint
☐ compatible substrates
☐ correct primer
☐ correct joint dimensions
☐ current manufacturer instructions

4.10.4 MATERIAL CONTROL

Check:

- sealant;

- batch;

- shelf life;

- storage;

- backer rod;

- bond breaker;

- primer;

- cleaner;

- compatibility.

4.10.5 INSPECTION

Joint preparation

Check:

- clean;

- dry;

- sound;

- contaminants removed;

- proper depth/width.

Backer rod

Check:

- correct size;

- correct depth;

- not damaged;

- no three-sided adhesion where prohibited.

Primer

Verify where required.

Application

Check:

- continuous bead;

- no voids;

- full contact;

- correct depth;

- correct profile.

Adhesion

Inspect:

- no edge separation;

- no bubbles;

- no tearing.

Finish/tooling

Check:

- smooth;

- proper concave profile where specified;

- clean edges;

- aesthetically acceptable.

4.10.6 RECORDS

Capture:

- joint/location;

- product;

- batch;

- weather where required;

- substrate;

- adhesion tests;

- photos;

- repairs.

4.10.7 NC / DEFICIENCY

Common:

- wrong sealant;

- expired material;

- dirty substrate;

- missing primer;

- wrong joint depth;

- missing backer rod;

- three-sided adhesion;

- voids;

- poor tooling;

- adhesion failure;

- cracks.

4.10.8 CORRECTIVE ACTION — EXAMPLE

Sealant pulls away from masonry during adhesion test.

Identify area → review substrate prep/primer/product compatibility → remove failed sealant → prepare joint properly → reprime if required → reinstall → retest adhesion → document.

4.10.9 VERIFICATION

Confirm:

- joint cleaned;

- correct materials;

- geometry correct;

- adhesion acceptable;

- finish complete.

4.10.10 CLOSURE

☐ correct product
☐ substrate accepted
☐ backer rod correct
☐ primer applied where required
☐ joint geometry correct
☐ application continuous
☐ adhesion accepted
☐ finish accepted
☐ testing complete

4.10.11 REPORTING / ANALYSIS

Track:

- recurring adhesion failures;

- poor substrate preparation;

- weather-related issues;

- repeated joint geometry problems;

- recurring installer workmanship problems.

4.10.12 QUALITY CHECKPOINT

☐ Correct product
☐ Compatibility
☐ Substrate preparation
☐ Joint width/depth
☐ Backer rod
☐ Primer
☐ Continuous bead
☐ Adhesion
☐ Tooling
☐ Appearance
☐ Testing/repair closure

BUILDING ENVELOPE — MASTER PRE-CONCEALMENT GATE

Before any major layer gets covered, ask:

DOCUMENTS

☐ Latest detail
☐ Approved products
☐ Approved shop drawings
☐ Manufacturer instructions
☐ Technical changes incorporated

SUBSTRATE

☐ Clean
☐ Dry as required
☐ Sound
☐ Correct geometry
☐ Openings correct

AIR / VAPOUR CONTROL

☐ Membranes continuous
☐ Seams complete
☐ Transitions complete
☐ Penetrations sealed
☐ Repairs complete

THERMAL

☐ Correct insulation
☐ Thickness correct
☐ No gaps
☐ No compression
☐ Dry and undamaged

WATER MANAGEMENT

☐ Flashing complete
☐ Drainage path clear
☐ Weeps open
☐ Sills/heads correct
☐ No trapped water path

OPENINGS

☐ Windows integrated
☐ Doors integrated
☐ Perimeter seals complete

EXTERIOR FINISH

☐ Cladding/masonry supports correct
☐ Anchors/fasteners correct
☐ Joints correct
☐ Sealants correct

EVIDENCE

☐ Photos
☐ Inspection forms
☐ Tests
☐ Repairs
☐ Pre-concealment release

BUILDING ENVELOPE — INTERFACE CHECK

This one should probably become a dedicated screen in the app.

Every time you inspect the envelope, check these interface zones:

Wall ↔ Foundation
Wall ↔ Roof
Wall ↔ Window
Wall ↔ Door
Wall ↔ Structural Steel
Wall ↔ Concrete
Wall ↔ Mechanical penetration
Wall ↔ Electrical penetration
Masonry ↔ Flashing
Cladding ↔ Opening
Insulation ↔ Structure
Air barrier ↔ Opening membrane
Sealant ↔ adjacent materials

Why?

Because a large number of envelope failures happen between systems, not within the middle of one system.

PRACTICAL EXAMPLE — WINDOW + WALL INTERFACE

Suppose tomorrow the contractor is installing 12 windows.

Your playbook tells you to inspect not just the window.

Before installation

Check:

- approved window shop drawing;

- current wall detail;

- opening dimension;

- air barrier;

- sill membrane;

- flashing;

- anchor requirements;

- sealant system;

- testing requirement.

During installation

Check:

- correct unit;

- shimming;

- anchoring;

- level/plumb;

- perimeter clearance.

Before exterior concealment

Check:

- sill flashing;

- jamb transitions;

- head flashing;

- air barrier transition;

- water seal;

- insulation around frame;

- drainage path.

After sealant

Check:

- backer rod;

- joint dimensions;

- adhesion;

- tooling.

Testing

If field water testing is required:

- witness test;

- record result;

- identify failure;

- repair;

- retest.

Closure

Only then is:

Window W-07 = quality complete

rather than merely:

“Window installed.”

BUILD 2 — BUILDING ENVELOPE STATUS

4.1 Exterior Wall Assemblies ✓
4.2 Air Barrier ✓
4.3 Vapour Barrier ✓
4.4 Thermal Insulation ✓
4.5 Exterior Sheathing ✓
4.6 Exterior Masonry/Veneer ✓
4.7 Exterior Cladding/Panels ✓
4.8 Windows/Glazing ✓
4.9 Exterior Doors ✓
4.10 Sealants ✓

The building envelope module is now structurally complete.

Yes. Roofing should absolutely remain its own first-class quality system. It behaves differently from vertical envelope work because you are dealing with horizontal drainage, ponding risk, weather exposure, penetrations, curbs, membrane continuity, sequencing, and often a very narrow inspection window before layers are concealed.

The governing principle remains:

CRT/Hydro-Québec drawings, devis, Plan Qualité, PIE/PRIE, approved shop drawings, manufacturer instructions, approved procedures, technical directives, and applicable project standards govern.
This playbook tells you how to control the work systematically so the roof is not merely “installed,” but traceably accepted.

5. ROOFING

The overall quality objective is:

Create a continuous, durable roof assembly that controls air, vapour, heat and water, drains as designed, integrates correctly with penetrations and equipment, and remains fully traceable through inspection, testing and closure.

The most important roofing principles for QC are:

continuity → drainage → sequencing → compatibility → penetration control → pre-concealment verification → testing → repair verification.

5.1 ROOF DECK / SUBSTRATE

Quality objective

Provide a structurally suitable, clean, dry, correctly sloped and dimensionally acceptable substrate for the roof assembly above it.

A membrane installed perfectly over a bad substrate can still fail.

5.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- roof plans;

- structural roof framing/deck drawings;

- roof sections/details;

- roof specification;

- deck specification;

- slope requirements;

- drainage layout;

- approved shop drawings;

- manufacturer substrate requirements;

- equipment-curb details;

- penetration details;

- Plan Qualité;

- PIE/PRIE;

- technical changes;

- QMT/RFI responses;

- temporary-weather-protection requirements.

Extract:

- deck type;

- thickness/gauge;

- fastening;

- support spacing;

- slope;

- elevation;

- openings;

- curbs;

- substrate condition requirements;

- flatness/tolerance;

- moisture limits;

- repair requirements.

5.1.2 PLANNING

Before roofing begins:

- confirm structural/deck work complete enough;

- identify roof zones;

- identify permanent slopes;

- identify roof drains;

- identify curbs/penetrations;

- identify areas that will become inaccessible once roofing starts;

- coordinate roof sequencing with MEP/electrical trades.

Critical planning question:

Is everybody who needs to penetrate the roof finished or coordinated before we close the membrane?

Late penetrations are one of the most common ways a good roof gets damaged.

5.1.3 DOCUMENT CONTROL

Verify:

☐ latest roof plan
☐ latest structural/deck drawing
☐ latest drain layout
☐ latest equipment-curb layout
☐ latest penetration locations
☐ current roof assembly detail
☐ current manufacturer instructions
☐ current technical changes
☐ current PIE/PRIE

5.1.4 MATERIAL CONTROL

For deck/substrate-related materials, verify:

- correct deck type;

- correct thickness/gauge;

- approved fasteners;

- approved repair material;

- primers;

- patch materials;

- temporary protection.

5.1.5 INSPECTION / TESTING

Deck condition

Check:

- clean;

- dry;

- structurally sound;

- no loose debris;

- no oil/contaminants;

- no sharp projections;

- no damaged areas;

- no unsupported edges.

Fastening

Where applicable:

- correct fastener;

- correct spacing;

- properly seated;

- missing fasteners;

- overdriven/loose fasteners.

Geometry

Verify:

- slope;

- elevation;

- drain depressions;

- openings;

- curb locations;

- edge conditions.

Surface suitability

Ask:

Can the next roofing layer be installed without bridging, puncturing, rocking, trapping water or creating discontinuity?

5.1.6 RECORDS / EVIDENCE

Capture:

- roof zone;

- deck type;

- condition;

- fastening inspection;

- slope/elevation verification;

- openings;

- curb locations;

- defects;

- corrective work;

- pre-roofing acceptance photos.

5.1.7 NC / DEFICIENCY

Typical:

- damaged deck;

- wet substrate;

- wrong slope;

- missing fasteners;

- excessive openings;

- incorrect curb location;

- debris;

- sharp edges;

- unresolved structural defect.

5.1.8 CORRECTIVE ACTION — EXAMPLE

Deck area near drain is low and likely to create ponding.

Identify exact zone → verify roof slope/detail → survey/measure → notify → obtain approved correction → repair/rebuild slope → reinspect → record before membrane proceeds.

5.1.9 VERIFICATION

Confirm:

- repair complete;

- geometry corrected;

- surface acceptable;

- no new damage;

- drain interface correct.

5.1.10 CLOSURE

☐ deck accepted
☐ slope accepted
☐ openings coordinated
☐ curbs coordinated
☐ drains ready
☐ substrate clean/dry
☐ defects closed
☐ ready for roof assembly

5.1.11 REPORTING / ANALYSIS

Track:

- recurring deck damage;

- late penetration changes;

- poor slope;

- recurring wet substrate;

- opening/curb coordination errors.

5.1.12 QUALITY CHECKPOINT

☐ Correct deck
☐ Fastening
☐ Clean
☐ Dry
☐ Sound
☐ Correct slope
☐ Openings correct
☐ Curbs correct
☐ Drains coordinated
☐ Ready for next layer

5.2 VAPOUR / AIR CONTROL LAYER

This layer may be the roof air barrier, vapour retarder, or part of a combined system depending on design.

Quality objective

Create a continuous roof air/vapour-control layer that is correctly located, bonded/sealed, integrated with wall control layers, and not damaged before insulation/membrane conceal it.

5.2.1 REQUIREMENTS

Obtain:

- roof assembly details;

- wall-to-roof transition details;

- approved membrane;

- primer;

- seam/lap requirements;

- penetration details;

- curb details;

- manufacturer instructions;

- compatibility requirements;

- temperature limits;

- substrate requirements;

- PIE/PRIE.

5.2.2 PLANNING

Identify:

- sequence relative to wall air barrier;

- drain penetrations;

- conduits;

- pipes;

- curbs;

- roof edges;

- parapets;

- temporary penetrations.

Plan inspection before insulation covers it.

5.2.3 DOCUMENT CONTROL

Verify:

☐ correct membrane
☐ correct location in assembly
☐ latest roof/wall transition detail
☐ correct primer
☐ penetration details
☐ approved repair method

5.2.4 MATERIAL CONTROL

Check:

- membrane;

- primer;

- tape;

- sealant;

- transition membrane;

- accessory materials;

- shelf life;

- storage;

- compatibility.

5.2.5 INSPECTION / TESTING

Substrate

- clean;

- dry;

- sound;

- acceptable temperature;

- free of sharp projections.

Membrane

Check:

- continuous installation;

- full adhesion;

- seams;

- laps;

- corners;

- penetrations;

- curbs;

- wall transition;

- drains;

- repairs.

Continuity

This is critical:

Roof air barrier must connect continuously to wall air barrier.

A perfect roof membrane with a discontinuous parapet transition can still create serious air leakage.

5.2.6 RECORDS / EVIDENCE

Capture:

- zone;

- product;

- substrate;

- weather/temp where required;

- seams;

- penetrations;

- curbs;

- parapets;

- wall transition;

- repairs;

- pre-concealment acceptance.

5.2.7 NC / DEFICIENCY

Common:

- open seam;

- puncture;

- poor adhesion;

- missing transition;

- unsealed penetration;

- membrane installed over wet deck;

- insulation placed before inspection.

5.2.8 CORRECTIVE ACTION

Example:

Air/vapour layer discontinuous around mechanical curb.

Expose as needed → identify approved curb detail → install compatible transition membrane/sealant → inspect continuity → photograph → release insulation.

5.2.9 VERIFICATION

Confirm repaired continuity and adhesion.

5.2.10 CLOSURE

☐ correct membrane
☐ seams complete
☐ penetrations sealed
☐ curbs integrated
☐ parapets integrated
☐ wall transition complete
☐ repairs accepted
☐ evidence complete

5.2.11 REPORTING / ANALYSIS

Track recurring damage from later trades or poor curb coordination.

5.2.12 QUALITY CHECKPOINT

☐ Substrate ready
☐ Product correct
☐ Seams/laps
☐ Penetrations
☐ Curbs
☐ Parapets
☐ Roof-wall transition
☐ Damage repaired
☐ Pre-concealment release

5.3 ROOF INSULATION

Quality objective

Install the correct insulation type and thickness in the required layering pattern, with continuity, secure attachment and designed slope toward drainage points.

5.3.1 REQUIREMENTS

Obtain:

- roof plan;

- roof assembly details;

- insulation specification;

- tapered insulation layout;

- approved product data;

- fastening/adhesive requirements;

- manufacturer instructions;

- drain details;

- R-value requirements;

- technical changes;

- PIE/PRIE.

Extract:

- insulation type;

- thickness;

- number of layers;

- taper;

- slope;

- stagger pattern;

- fastening;

- adhesive;

- cover board if used;

- thermal resistance.

5.3.2 PLANNING

Before installation:

- identify roof zone;

- know tapered layout;

- coordinate drains;

- coordinate curbs;

- confirm underlying membrane accepted;

- sequence work to avoid exposing insulation to rain.

High-priority issue

Wet roof insulation can compromise the entire assembly.

So weather planning matters.

5.3.3 DOCUMENT CONTROL

Verify:

☐ correct roof assembly
☐ correct insulation type
☐ correct thickness
☐ tapered layout current
☐ drain sump detail
☐ fastening pattern
☐ technical changes incorporated

5.3.4 MATERIAL CONTROL

Check:

- product;

- thickness;

- density/type;

- R-value;

- taper designation;

- damage;

- wetness;

- crushed edges;

- storage protection;

- correct fasteners/adhesives.

Reject/control visibly wet or damaged material according to project requirements.

5.3.5 INSPECTION / TESTING

Product

Correct type and thickness.

Layers

Check:

- required number of layers;

- joints staggered;

- no aligned through-joints unless permitted.

Staggering

Verify proper offset between layers.

Attachment

Check:

- fastener type;

- quantity;

- spacing;

- plate installation;

- adhesive coverage where used.

Slopes

Verify:

- taper direction;

- positive drainage;

- saddles/crickets;

- drain sump geometry;

- no obvious low areas.

Continuity

Look for:

- gaps;

- missing pieces;

- compressed/damaged boards;

- poorly cut penetrations.

5.3.6 RECORDS / EVIDENCE

Capture:

- roof zone;

- product;

- thickness;

- layer sequence;

- tapered insulation;

- fasteners/adhesive;

- drain zones;

- gaps/repairs;

- photos before membrane concealment.

5.3.7 NC / DEFICIENCY

Common:

- wrong insulation;

- wrong thickness;

- wet insulation;

- missing layer;

- joints not staggered;

- gaps;

- crushed boards;

- wrong taper;

- poor attachment;

- slope away from drain.

5.3.8 CORRECTIVE ACTION — EXAMPLE

Tapered insulation installed in reverse direction near drain.

Identify area → compare taper plan → remove affected boards → reinstall correct sequence → verify slope → photograph → release membrane installation.

5.3.9 VERIFICATION

Confirm:

- correct thickness;

- slope;

- continuity;

- dryness;

- attachment.

5.3.10 CLOSURE

☐ correct product
☐ thickness correct
☐ layers complete
☐ staggered joints
☐ attachment correct
☐ slopes correct
☐ drains/crickets coordinated
☐ no wet/damaged material
☐ ready for membrane

5.3.11 REPORTING / ANALYSIS

Track:

- wet material;

- recurring taper errors;

- gaps;

- poor fastener patterns;

- storage failures.

5.3.12 QUALITY CHECKPOINT

☐ Product
☐ Thickness
☐ Layers
☐ Staggering
☐ Attachment
☐ Taper
☐ Drainage slope
☐ Gaps
☐ Dry condition
☐ Pre-concealment evidence

5.4 ROOFING MEMBRANE

This is the primary water-control layer.

Quality objective

Install a continuous, fully integrated roofing membrane using the approved system, with compliant seams, laps, adhesion/fastening and transitions, free of damage and defects.

5.4.1 REQUIREMENTS

Obtain:

- roofing specification;

- membrane type;

- approved product;

- manufacturer instructions;

- lap/seam requirements;

- fastening/adhesive requirements;

- environmental limits;

- substrate requirements;

- flashing details;

- penetration details;

- curb details;

- warranty requirements;

- testing requirements;

- PIE/PRIE.

5.4.2 PLANNING

Before membrane installation:

- confirm insulation/cover board accepted;

- review weather forecast;

- determine daily closure plan;

- identify penetrations;

- coordinate curbs;

- identify temporary seams;

- plan testing;

- ensure no later trade will unnecessarily damage membrane.

Daily closure concept

Roofing work should not leave water paths open overnight or during rain.

The exact closure detail comes from the approved roofing procedure/manufacturer.

5.4.3 DOCUMENT CONTROL

Verify:

☐ correct membrane
☐ correct system
☐ current details
☐ approved adhesive/fasteners
☐ seam requirements
☐ environmental limits
☐ warranty requirements

5.4.4 MATERIAL CONTROL

Check:

- membrane rolls/sheets;

- adhesive;

- primer;

- fasteners;

- plates;

- flashing membrane;

- sealant;

- cleaner;

- accessories;

- shelf life;

- storage;

- damage.

5.4.5 INSPECTION / TESTING

Substrate

Check:

- dry;

- clean;

- smooth;

- firmly attached;

- no gaps;

- no projections.

Application

Verify:

- proper sheet orientation;

- no trapped debris;

- no wrinkles;

- appropriate adhesive coverage where applicable.

Laps

Check:

- required overlap;

- alignment;

- clean interface.

Seams

Depending on system:

- heat-welded;

- adhesive;

- taped;

- otherwise specified.

Check:

- continuity;

- full bonding;

- no fishmouths;

- no voids.

Adhesion

Check:

- full contact;

- no bubbles;

- no delamination.

Fastening

Check:

- type;

- spacing;

- edge/corner requirements;

- secure installation.

Damage

Look for:

- punctures;

- cuts;

- burns;

- abrasions;

- construction traffic damage.

5.4.6 RECORDS / EVIDENCE

Capture:

- roof zone;

- membrane product;

- installation date;

- weather;

- seams;

- laps;

- fastener pattern where relevant;

- repairs;

- penetration areas;

- photos;

- manufacturer inspection reports;

- testing results.

5.4.7 NC / DEFICIENCY

Common:

- insufficient lap;

- failed seam;

- puncture;

- wrinkle;

- blister;

- poor adhesion;

- wrong fastener spacing;

- wet substrate covered;

- incompatible material;

- open daily termination.

5.4.8 CORRECTIVE ACTION — EXAMPLE

Probe/testing identifies defective welded seam.

Mark exact extent → open/prepare area per approved repair method → reweld/patch → reinspect/probe → document repair → close.

5.4.9 VERIFICATION

Confirm:

- repair extends beyond defect as required;

- seam intact;

- membrane continuous;

- no new damage;

- testing acceptable.

5.4.10 CLOSURE

☐ membrane complete
☐ seams accepted
☐ laps accepted
☐ attachment accepted
☐ penetrations integrated
☐ flashings integrated
☐ repairs complete
☐ testing complete
☐ warranty/manufacturer requirements satisfied

5.4.11 REPORTING / ANALYSIS

Track:

- recurring seam failures;

- punctures by later trades;

- adhesion failures;

- wet substrate events;

- installer workmanship trends.

5.4.12 QUALITY CHECKPOINT

☐ Correct membrane
☐ Substrate dry/ready
☐ Application correct
☐ Laps correct
☐ Seams complete
☐ Adhesion
☐ Fasteners
☐ No damage
☐ Repairs
☐ Testing

5.5 FLASHINGS & TERMINATIONS

Quality objective

Ensure the roofing membrane terminates and transitions properly at edges, walls, parapets, joints and changes in plane so water cannot bypass the roof system.

5.5.1 REQUIREMENTS

Obtain:

- parapet details;

- edge details;

- wall transitions;

- metal flashing shop drawings;

- membrane flashing details;

- termination-bar details;

- counterflashing;

- sealants;

- fastening;

- manufacturer instructions;

- PIE/PRIE.

5.5.2 PLANNING

Identify all roof transitions:

- parapets;

- walls;

- expansion joints;

- edges;

- curbs;

- drains;

- roof-to-wall conditions.

5.5.3 DOCUMENT CONTROL

Verify:

☐ current detail
☐ flashing type
☐ height
☐ fastening
☐ overlap
☐ sealant
☐ termination detail

5.5.4 MATERIAL CONTROL

Check:

- membrane flashing;

- sheet metal;

- termination bars;

- fasteners;

- sealants;

- primers;

- compatibility.

5.5.5 INSPECTION

Check:

- flashing height;

- continuity;

- corners;

- overlaps;

- fastening;

- termination;

- counterflashing;

- end conditions;

- sealants;

- water-shedding orientation.

Critical field mindset

Ask:

If water reaches this point, where does it go?

If answer is unclear, investigate.

5.5.6 RECORDS

Capture representative and critical transitions before concealment.

5.5.7 NC / DEFICIENCY

Common:

- flashing too low;

- incomplete corner;

- reverse lap;

- open termination;

- missing fastener;

- sealant discontinuity;

- metal flashing allowing water behind membrane.

5.5.8 CORRECTIVE ACTION

Example:

Parapet corner flashing has open fishmouth.

Mark → repair using approved membrane detail → reinspect seam/corner → photograph → close.

5.5.9 VERIFICATION

Confirm continuity and secure termination.

5.5.10 CLOSURE

☐ all transitions complete
☐ corners complete
☐ terminations secure
☐ metal flashing complete
☐ sealants complete
☐ repairs closed

5.5.11 REPORTING

Track recurring corner/termination failures.

5.5.12 QUALITY CHECKPOINT

☐ Parapets
☐ Walls
☐ Edges
☐ Corners
☐ Expansion joints
☐ Termination bars
☐ Counterflashing
☐ Sealants
☐ Water shedding

5.6 ROOF PENETRATIONS

This is one of the highest-risk roof details.

Quality objective

Integrate every mechanical, electrical and structural penetration into the roof system without compromising waterproofing, air/vapour continuity, thermal continuity or drainage.

5.6.1 REQUIREMENTS

Obtain:

- roof penetration details;

- mechanical drawings;

- electrical drawings;

- structural drawings;

- equipment shop drawings;

- approved curb/penetration details;

- roofing manufacturer requirements;

- flashing/sealant details;

- insulation details;

- firestopping where applicable;

- PIE/PRIE.

5.6.2 PLANNING

Before roofing:

- identify every known penetration;

- compare architectural + mechanical + electrical drawings;

- coordinate late penetrations;

- ensure sleeves/curbs installed before membrane where possible.

Quality rule

Unplanned penetrations are controlled events.

Nobody should casually drill through completed roofing without coordinated details.

5.6.3 DOCUMENT CONTROL

Verify:

☐ penetration approved
☐ correct location
☐ correct sleeve/curb detail
☐ roofing detail current
☐ MEP change incorporated

5.6.4 MATERIAL CONTROL

Check:

- sleeves;

- curbs;

- boots;

- flashing membranes;

- sealants;

- collars;

- insulation;

- compatible materials.

5.6.5 INSPECTION

Check:

- penetration location;

- clearance;

- curb/sleeve height;

- membrane upturn;

- flashing;

- seam continuity;

- insulation around penetration;

- air/vapour continuity;

- sealant;

- mechanical support independent of membrane where required.

Watch for

- unsupported pipe stressing membrane;

- field-made sealant-only “repair”;

- membrane cut too large;

- water-trapping geometry.

5.6.6 RECORDS

Capture:

- penetration ID;

- service/system;

- location;

- detail;

- flashing;

- completed seal;

- testing/inspection.

5.6.7 NC / DEFICIENCY

Common:

- unapproved penetration;

- poor flashing;

- insufficient curb height;

- cut membrane;

- incompatible sealant;

- thermal gap;

- penetration in drainage low point;

- later trade damage.

5.6.8 CORRECTIVE ACTION — EXAMPLE

Electrical conduit added through finished membrane without approved flashing.

Control → document → identify detail requirement → coordinate roofing/electrical parties → install approved curb/boot/flashing → restore insulation/control layers → test/inspect → record closure.

5.6.9 VERIFICATION

Confirm:

- membrane continuity;

- flashing;

- air/vapour continuity;

- insulation;

- service support;

- watertight condition.

5.6.10 CLOSURE

☐ penetration approved
☐ correct location
☐ flashing complete
☐ membrane complete
☐ insulation restored
☐ seals complete
☐ testing accepted

5.6.11 REPORTING / ANALYSIS

Track:

- late penetrations;

- recurring MEP coordination problems;

- repeated membrane damage.

5.6.12 QUALITY CHECKPOINT

☐ Approved penetration
☐ Correct opening
☐ Sleeve/curb
☐ Membrane flashing
☐ Seams
☐ Insulation
☐ Air/vapour continuity
☐ Sealant
☐ Service support
☐ Testing/closure

5.7 CURBS & EQUIPMENT INTERFACES

Quality objective

Ensure rooftop equipment curbs are correctly located, dimensioned, elevated, anchored, insulated and flashed so the equipment can be installed without compromising roof performance.

5.7.1 REQUIREMENTS

Obtain:

- mechanical/equipment drawings;

- structural support details;

- curb shop drawings;

- roof details;

- manufacturer requirements;

- curb height requirements;

- insulation;

- flashing;

- anchorage;

- equipment clearances;

- PIE/PRIE.

5.7.2 PLANNING

Before curb installation:

- verify equipment model;

- curb dimensions;

- opening;

- support;

- orientation;

- service connections;

- drainage relationship.

5.7.3 DOCUMENT CONTROL

Verify:

☐ correct curb/equipment pair
☐ current shop drawing
☐ structural support
☐ roof detail
☐ location/orientation

5.7.4 MATERIAL CONTROL

Check:

- curb;

- anchors;

- insulation;

- blocking;

- flashing;

- gasket/seal;

- corrosion protection.

5.7.5 INSPECTION

Check:

- location;

- dimensions;

- orientation;

- elevation/height;

- level;

- anchorage;

- structural support;

- insulation;

- flashing;

- membrane integration;

- equipment clearance.

5.7.6 RECORDS

Capture:

- curb ID;

- equipment ID;

- location;

- dimensions;

- anchor inspection;

- flashing;

- final interface.

5.7.7 NC / DEFICIENCY

Common:

- wrong curb size;

- wrong orientation;

- low curb;

- inadequate anchorage;

- poor flashing;

- thermal break;

- interference with drain/other equipment.

5.7.8 CORRECTIVE ACTION

Example:

Mechanical unit curb rotated 90° from approved shop drawing.

Stop equipment installation → verify shop drawing → reposition/rework curb as authorized → repair roofing → reinspect geometry/flashing → close.

5.7.9 VERIFICATION

Confirm:

- location;

- orientation;

- height;

- anchorage;

- flashing;

- roof continuity.

5.7.10 CLOSURE

☐ curb correct
☐ support accepted
☐ anchors accepted
☐ insulation complete
☐ roofing integrated
☐ equipment can be installed

5.7.11 REPORTING / ANALYSIS

Track recurring MEP/roof coordination problems.

5.7.12 QUALITY CHECKPOINT

☐ Equipment ID
☐ Curb ID
☐ Dimensions
☐ Orientation
☐ Location
☐ Height
☐ Anchorage
☐ Insulation
☐ Flashing
☐ Roof integration

5.8 ROOF DRAINS

Quality objective

Ensure roof drains are correctly located, set at the proper elevation, securely connected and fully integrated with the roofing membrane so water reaches the drainage system without ponding or leakage.

5.8.1 REQUIREMENTS

Obtain:

- roof drainage plan;

- mechanical/plumbing drawings;

- drain details;

- slope/taper plan;

- membrane drain detail;

- drain manufacturer data;

- overflow details where applicable;

- testing requirements;

- PIE/PRIE.

5.8.2 PLANNING

Before insulation/membrane:

- confirm drain location;

- confirm piping below;

- coordinate drain bowl;

- coordinate sump;

- verify taper;

- identify overflow paths.

5.8.3 DOCUMENT CONTROL

Verify:

☐ correct drain
☐ correct location
☐ elevation
☐ taper/sump
☐ membrane clamping/flashing detail
☐ piping connection

5.8.4 MATERIAL CONTROL

Check:

- drain body;

- clamping ring;

- dome/strainer;

- gaskets;

- insulation;

- flashing membrane;

- fasteners.

5.8.5 INSPECTION

Location

Correct point on roof.

Elevation

Drain should function as low point according to design.

Connection

Verify:

- secure;

- correct piping;

- no obvious leakage.

Membrane integration

Check:

- membrane properly dressed into drain;

- clamping ring;

- no wrinkles;

- no trapped membrane;

- seal complete.

Surrounding slope

Verify water can actually reach drain.

Overflow

Check where applicable.

5.8.6 RECORDS

Capture:

- drain ID;

- location;

- elevation;

- sump;

- membrane detail;

- final drain condition;

- testing.

5.8.7 NC / DEFICIENCY

Common:

- drain too high;

- wrong location;

- poor membrane clamp;

- blocked drain;

- inadequate sump;

- disconnected/leaking pipe;

- ponding around drain.

5.8.8 CORRECTIVE ACTION — EXAMPLE

Finished membrane slopes to a low point 1.5 m away from drain.

Survey/observe → document ponding geometry → compare taper plan → obtain authorized correction → rework insulation/membrane as required → retest drainage → document.

5.8.9 VERIFICATION

Confirm:

- drain is functional low point;

- membrane sealed;

- water flows;

- no leakage;

- strainer installed.

5.8.10 CLOSURE

☐ correct drain
☐ correct elevation
☐ connection complete
☐ membrane integrated
☐ sump correct
☐ drainage functional
☐ test complete

5.8.11 REPORTING / ANALYSIS

Track recurring ponding or drain-elevation issues.

5.8.12 QUALITY CHECKPOINT

☐ Drain ID
☐ Location
☐ Elevation
☐ Pipe connection
☐ Sump/taper
☐ Membrane clamp
☐ Strainer
☐ Overflow
☐ Drainage test

5.9 ROOFING TESTING / FINAL INSPECTION

Quality objective

Demonstrate that the completed roofing system is continuous, watertight, properly drained, free of unresolved damage and ready for acceptance/warranty.

This is the final roof quality gate.

5.9.1 REQUIREMENTS

Obtain:

- roof testing specification;

- manufacturer warranty requirements;

- water-test procedure if specified;

- electronic leak detection requirements;

- flood-test limitations;

- inspection frequency;

- final acceptance criteria;

- deficiency process;

- PIE/PRIE.

5.9.2 PLANNING

Before testing:

- membrane installation complete enough;

- drains operational;

- penetrations complete;

- flashings complete;

- curbs complete;

- roof cleaned;

- test zones defined;

- testing contractor/manufacturer coordinated.

5.9.3 DOCUMENT CONTROL

Verify:

☐ approved testing method
☐ latest roof layout
☐ test zones
☐ warranty requirements
☐ deficiency closure process

5.9.4 MATERIAL CONTROL

Limited at this stage, but ensure repair materials remain approved/available.

5.9.5 INSPECTION / TESTING

A. Final visual inspection

Inspect:

- membrane field;

- seams;

- flashings;

- parapets;

- penetrations;

- curbs;

- drains;

- sealants;

- repairs;

- debris;

- traffic damage.

B. Membrane integrity

Where required:

- seam probing;

- electronic leak detection;

- other specified method.

C. Drainage

Observe:

- positive drainage;

- no significant unintended ponding;

- drains clear;

- overflow functioning where applicable.

D. Water testing

If specified:

- follow approved method;

- identify test zone;

- control duration;

- monitor interior for leakage;

- record result.

Do not flood-test unless specifically permitted by the project/roof design.

E. Deficiency survey

Create location-specific list:

- punctures;

- open seams;

- incomplete flashing;

- damaged coating;

- sealant defects;

- ponding;

- drain issues.

5.9.6 RECORDS / EVIDENCE

Retain:

- final inspection checklist;

- roof plan marked with deficiencies;

- photographs;

- electronic test report;

- water-test report;

- manufacturer inspection report;

- repair records;

- retest results;

- warranty documents where applicable.

5.9.7 NC / DEFICIENCY

Potential final issues:

- failed leak test;

- open seam;

- puncture;

- unresolved ponding;

- incomplete flashing;

- damaged penetration detail;

- drain blockage;

- missing warranty inspection.

5.9.8 CORRECTIVE ACTION — EXAMPLE

Electronic leak detection identifies membrane breach beneath recently completed equipment work.

Locate defect → mark exact location → document → repair using approved system → reinspect → repeat electronic test → obtain passing result → close.

5.9.9 VERIFICATION

Every repair requires:

- physical reinspection;

- testing/retest where required;

- updated deficiency status;

- evidence.

5.9.10 CLOSURE

Roofing closes only when:

☐ membrane visually accepted
☐ seams accepted
☐ flashings complete
☐ penetrations complete
☐ curbs complete
☐ drains operational
☐ drainage accepted
☐ testing passed
☐ deficiencies repaired
☐ repairs retested where required
☐ manufacturer/warranty requirements complete
☐ final records filed

5.9.11 REPORTING / ANALYSIS

Final roofing analysis should identify:

- number/type of deficiencies;

- leak-test failures;

- recurring installer issues;

- damage caused by other trades;

- recurrent problem details;

- open warranty items;

- risk areas requiring future observation.

5.9.12 FINAL ROOF QUALITY CHECKPOINT

ASSEMBLY

☐ Deck/substrate accepted
☐ Air/vapour layer accepted
☐ Insulation accepted
☐ Membrane accepted
☐ Flashings accepted
☐ Penetrations accepted
☐ Curbs accepted
☐ Drains accepted

PERFORMANCE

☐ Drainage works
☐ No unintended ponding
☐ Integrity testing passed
☐ Water testing passed where specified
☐ No unresolved leakage

DOCUMENTATION

☐ Material approvals
☐ Inspection records
☐ Photos
☐ Test reports
☐ Repair records
☐ Warranty/manufacturer records
☐ Deficiency closure

ROOFING MASTER PRE-CONCEALMENT GATES

Roofing has several inspection windows. I would explicitly build these into the app.

Gate 1 — Before air/vapour layer

☐ Deck accepted
☐ Openings/curbs correct
☐ Drains coordinated
☐ Surface clean/dry

Gate 2 — Before insulation conceals air/vapour layer

☐ Membrane continuous
☐ Seams complete
☐ Penetrations sealed
☐ Wall/parapet transitions complete
☐ Repairs closed

Gate 3 — Before roofing membrane conceals insulation

☐ Correct insulation
☐ Thickness
☐ Taper/slope
☐ Fastening
☐ No wet boards
☐ Drain sumps correct

Gate 4 — Before equipment/traffic obscures final membrane

☐ Membrane complete
☐ Seams accepted
☐ Flashings complete
☐ Penetrations complete
☐ Curbs complete
☐ Drains complete

Gate 5 — Final acceptance

☐ Testing
☐ Drainage
☐ Deficiencies
☐ Repairs
☐ Retesting
☐ Warranty documentation

PRACTICAL EXAMPLE — ROOFTOP HVAC UNIT

Suppose tomorrow an HVAC unit is being installed on a completed roof.

You don't only inspect the equipment.

You open:

Roofing → Curbs & Equipment Interfaces
then cross-reference
Roofing → Penetrations
and possibly
Mechanical → HVAC Equipment

Your workflow becomes:

Before equipment arrives

Check:

- correct unit;

- correct curb;

- correct location;

- structural support;

- curb height;

- curb insulation;

- membrane flashing;

- nearby drain;

- electrical/mechanical penetrations;

- shop drawings.

During installation

Check:

- unit orientation;

- bearing;

- fastening;

- gasket/seal;

- no roof membrane damage;

- service clearances.

After installation

Check:

- membrane still intact;

- penetrations sealed;

- roofing repairs completed;

- no blocked drainage;

- no loose fasteners/debris;

- test/commissioning interface ready.

Now you have controlled both:

equipment quality and roof-envelope integrity.

That is exactly why the system is organized by construction activity but allows cross-module interfaces.

BUILD 2 — ROOFING STATUS

5.1 Roof Deck/Substrate ✓
5.2 Vapour/Air Control Layer ✓
5.3 Roof Insulation ✓
5.4 Roofing Membrane ✓
5.5 Flashings & Terminations ✓
5.6 Roof Penetrations ✓
5.7 Curbs & Equipment Interfaces ✓
5.8 Roof Drains ✓
5.9 Roofing Testing/Final Inspection ✓

Yes. We’ll keep the same field-execution structure and make Interior Architectural Construction just as operational as the previous modules.

The governing rule remains:

CRT/Hydro-Québec drawings, devis, Plan Qualité, PIE/PRIE, approved shop drawings, manufacturer instructions, fire/life-safety requirements, technical directives, and applicable project standards govern.
This playbook ensures you systematically identify the requirements, plan the work, control documents and materials, inspect before concealment, capture evidence, manage deficiencies/NCs, verify corrections, and close the quality loop.

6. INTERIOR ARCHITECTURAL CONSTRUCTION

The overall quality objective is:

Construct interior assemblies that are dimensionally correct, properly coordinated with services, compliant with acoustic/fire/moisture requirements, complete before concealment, and fully functional at turnover.

The critical mindset for interiors is:

coordination → concealed work → fire continuity → dimensional accuracy → finish readiness → operability

6.1 INTERIOR MASONRY

Quality objective

Construct interior masonry walls with the correct units, mortar, reinforcement, anchors, openings and geometry, while maintaining required fire/acoustic performance and coordination with adjacent work.

6.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- architectural floor plans;

- wall type schedules;

- masonry wall details;

- structural details where reinforced;

- fire-rated assembly details;

- door/frame details;

- MEP opening/penetration drawings;

- masonry specifications;

- block/unit approvals;

- mortar/grout requirements;

- reinforcement details;

- anchors/ties;

- lintel details;

- control-joint details;

- approved shop drawings;

- PIE/PRIE;

- technical changes;

- QMT/RFI responses.

Extract:

- wall type;

- unit size/type;

- wall thickness;

- fire rating;

- acoustic requirement;

- reinforcement;

- grout;

- anchors;

- lintels;

- openings;

- control joints;

- wall height;

- tolerances;

- interface conditions.

6.1.2 PLANNING

Before work:

- identify wall types by room/zone;

- coordinate door openings;

- coordinate MEP penetrations;

- identify reinforced/grouted cells;

- identify lintels;

- plan inspection before grout or concealment;

- verify backing/interface requirements;

- coordinate top-of-wall condition.

6.1.3 DOCUMENT CONTROL

Verify:

☐ correct floor plan
☐ correct wall type
☐ current fire-rating detail
☐ current reinforcement/lintel detail
☐ current MEP penetration layout
☐ latest revisions incorporated

6.1.4 MATERIAL CONTROL

Check:

- block/unit type;

- dimensions;

- condition;

- mortar type;

- grout;

- reinforcement;

- anchors/ties;

- lintels;

- fire/acoustic sealants;

- certificates where required.

6.1.5 INSPECTION / TESTING

Check:

- wall location;

- thickness;

- line/level/plumb;

- coursing;

- mortar joints;

- reinforcement;

- grout;

- anchors;

- lintels;

- openings;

- control joints;

- top-of-wall condition;

- penetrations;

- fire/acoustic continuity;

- housekeeping/cleanliness.

6.1.6 RECORDS / EVIDENCE

Capture:

- wall ID/room;

- wall type;

- reinforcement before grout;

- lintels;

- openings;

- anchors;

- fire-related interfaces;

- photos;

- inspection records;

- test results where required.

6.1.7 NC / DEFICIENCY

Typical:

- wrong block type;

- out-of-plumb wall;

- missing reinforcement;

- ungrouted required cells;

- wrong opening;

- missing lintel;

- missing control joint;

- unsealed penetration;

- incorrect top-of-wall detail.

6.1.8 CORRECTIVE ACTION — EXAMPLE

Door opening built 50 mm too narrow.

Measure → compare schedule/detail → control frame installation → correct masonry opening → verify lintel/reinforcement unaffected → remeasure → document closure.

6.1.9 VERIFICATION

Confirm:

- corrected geometry;

- fire/acoustic continuity;

- reinforcement/grout;

- opening dimensions;

- adjacent interfaces.

6.1.10 CLOSURE

☐ wall type correct
☐ geometry accepted
☐ openings correct
☐ reinforcement/grout complete
☐ anchors/lintels complete
☐ joints complete
☐ fire/acoustic interfaces complete
☐ records complete

6.1.11 REPORTING / ANALYSIS

Track:

- recurring opening errors;

- plumbness issues;

- missed reinforcement;

- penetration coordination failures;

- top-of-wall defects.

6.1.12 QUALITY CHECKPOINT

☐ Correct wall type
☐ Location
☐ Thickness
☐ Plumb/level
☐ Reinforcement
☐ Grout
☐ Lintels
☐ Openings
☐ Control joints
☐ Penetrations
☐ Fire/acoustic continuity
☐ Evidence complete

6.2 METAL STUD FRAMING

Quality objective

Install the correct stud-and-track framing in the right location, gauge, spacing and geometry, with sufficient backing/reinforcement and proper coordination for doors, ceilings, services and finishes.

6.2.1 REQUIREMENTS

🔵 Obtain:

- architectural plans;

- partition/wall type schedule;

- wall sections;

- reflected ceiling plans;

- door/window opening details;

- wall-height details;

- head-of-wall details;

- fire/acoustic assembly details;

- approved framing shop drawings if any;

- stud specifications;

- gauge/thickness requirements;

- fastener/anchor requirements;

- backing requirements;

- manufacturer instructions;

- MEP coordination drawings;

- PIE/PRIE.

Extract:

- stud type;

- gauge;

- spacing;

- wall height;

- track type;

- deflection head requirements;

- anchoring;

- openings;

- jamb reinforcement;

- backing;

- fire/acoustic assembly;

- coordination requirements.

6.2.2 PLANNING

Before framing:

- verify layout;

- identify wall types;

- coordinate door frames;

- identify heavy wall-mounted equipment requiring backing;

- coordinate MEP penetrations;

- coordinate ceiling heights;

- identify fire-rated walls;

- plan pre-concealment inspection before board.

6.2.3 DOCUMENT CONTROL

Verify:

☐ correct wall type
☐ correct stud gauge
☐ correct spacing
☐ correct head-of-wall detail
☐ current opening sizes
☐ current backing requirements
☐ MEP coordination current

6.2.4 MATERIAL CONTROL

Check:

- stud type/gauge;

- tracks;

- fasteners;

- anchors;

- clips;

- deflection track;

- backing;

- jamb studs;

- corrosion protection where required;

- damaged/bent members.

6.2.5 INSPECTION / TESTING

Layout

Check:

- wall location;

- dimensions;

- room size;

- door opening;

- alignment with structure/ceiling.

Studs

Check:

- correct gauge/type;

- spacing;

- orientation;

- full height;

- cuts/notches acceptable.

Tracks

Check:

- correct track;

- anchorage;

- alignment;

- deflection/head condition.

Openings

Check:

- door framing;

- jamb reinforcement;

- headers;

- clear dimensions.

Backing/reinforcement

Check for:

- cabinets;

- equipment;

- grab bars;

- handrails;

- wall-mounted devices;

- heavy services.

Coordination with services

Check:

- conduits;

- pipes;

- ducts;

- boxes;

- openings;

- no excessive unauthorized cutting.

6.2.6 RECORDS / EVIDENCE

Capture:

- wall/room;

- stud type/gauge;

- spacing;

- openings;

- backing;

- head-of-wall condition;

- service coordination;

- pre-board photos.

6.2.7 NC / DEFICIENCY

Common:

- wrong stud gauge;

- excessive spacing;

- mislocated wall;

- missing backing;

- wrong opening;

- poor anchorage;

- cut studs;

- missing deflection detail;

- service clashes.

6.2.8 CORRECTIVE ACTION — EXAMPLE

Wall-mounted electrical cabinet has no required backing.

Identify location → verify equipment/shop drawing → stop board closure → install approved backing → verify anchorage/support → photograph → release board installation.

6.2.9 VERIFICATION

Confirm:

- backing installed;

- framing geometry intact;

- services coordinated;

- fire/acoustic assembly preserved.

6.2.10 CLOSURE

☐ correct studs
☐ spacing correct
☐ tracks correct
☐ anchorage complete
☐ openings correct
☐ backing complete
☐ services coordinated
☐ head-of-wall correct
☐ ready for insulation/board

6.2.11 REPORTING / ANALYSIS

Track:

- repeated wrong gauge;

- missing backing;

- wall-layout errors;

- service conflicts;

- opening coordination issues.

6.2.12 QUALITY CHECKPOINT

☐ Wall layout
☐ Stud type/gauge
☐ Spacing
☐ Tracks
☐ Anchoring
☐ Head condition
☐ Openings
☐ Jamb reinforcement
☐ Backing
☐ MEP coordination
☐ Pre-concealment photos

6.3 INTERIOR INSULATION

Quality objective

Install the correct insulation continuously within interior assemblies to achieve the specified acoustic, thermal or fire-related performance without gaps, compression, moisture damage or coordination conflicts.

6.3.1 REQUIREMENTS

Obtain:

- wall type schedule;

- acoustic details;

- thermal details;

- fire-rated assembly details;

- insulation specifications;

- product approvals;

- manufacturer instructions;

- fire/acoustic test assembly references where applicable;

- PIE/PRIE.

Extract:

- insulation type;

- thickness;

- density;

- fire/acoustic properties;

- location;

- full-height requirements;

- continuity;

- installation method.

6.3.2 PLANNING

Before insulation:

- framing accepted;

- backing complete;

- MEP rough-in substantially complete;

- walls clean/dry;

- pre-concealment sequence planned.

6.3.3 DOCUMENT CONTROL

Verify:

☐ correct wall assembly
☐ correct insulation type
☐ correct thickness
☐ fire/acoustic assembly current
☐ technical changes incorporated

6.3.4 MATERIAL CONTROL

Check:

- product/type;

- thickness;

- density;

- condition;

- wetness;

- compression;

- damage;

- storage.

6.3.5 INSPECTION

Check:

- full cavity coverage;

- correct thickness;

- no gaps;

- no compression;

- no sagging;

- around boxes/penetrations;

- around framing;

- full-height continuity where required;

- no wet/damaged insulation.

6.3.6 RECORDS

Capture representative wall/zone photos before board.

6.3.7 NC / DEFICIENCY

Common:

- wrong insulation;

- missing cavity fill;

- compressed batt;

- gaps;

- wet material;

- incomplete acoustic/fire continuity.

6.3.8 CORRECTIVE ACTION

Example:

Acoustic batt omitted around multiple electrical boxes.

Open/hold closure → install correct insulation around boxes without compressing → reinspect → photograph → close.

6.3.9 VERIFICATION

Confirm full continuity and correct material.

6.3.10 CLOSURE

☐ correct product
☐ thickness correct
☐ full coverage
☐ no gaps/compression
☐ dry/undamaged
☐ ready for board closure

6.3.11 REPORTING / ANALYSIS

Track recurring missed cavities or rushed concealment.

6.3.12 QUALITY CHECKPOINT

☐ Type
☐ Thickness
☐ Full coverage
☐ Continuity
☐ Around services
☐ No compression
☐ No moisture
☐ Pre-concealment evidence

6.4 GYPSUM BOARD

Quality objective

Install the correct gypsum-board system in the required type, layers, orientation and fastening pattern, while maintaining fire, moisture, acoustic and finish requirements.

6.4.1 REQUIREMENTS

🔵 Obtain:

- wall type schedule;

- ceiling details;

- fire-rated assembly details;

- moisture-resistant area details;

- acoustic wall details;

- gypsum specifications;

- board type approvals;

- screw/fastener requirements;

- joint-treatment requirements;

- manufacturer instructions;

- PIE/PRIE.

Extract:

- board type;

- thickness;

- number of layers;

- orientation;

- staggering;

- fastener type/spacing;

- fire/moisture requirements;

- joint treatment;

- perimeter seal.

6.4.2 PLANNING

Before board:

- framing accepted;

- insulation complete;

- backing complete;

- MEP rough-in complete;

- required inspections completed;

- firestopping at concealed penetrations addressed;

- photos captured.

This is a major pre-concealment gate.

6.4.3 DOCUMENT CONTROL

Verify:

☐ correct wall type
☐ correct board type
☐ correct layers
☐ current fire-rated assembly
☐ current moisture requirements
☐ technical changes incorporated

6.4.4 MATERIAL CONTROL

Check:

- board type;

- thickness;

- edge condition;

- moisture exposure;

- damaged panels;

- fasteners;

- joint compound;

- tapes;

- sealants.

6.4.5 INSPECTION / TESTING

Board type

Verify correct board in:

- fire-rated walls;

- wet/moist areas;

- impact-resistant areas;

- shaft walls;

- ceilings.

Layers

Check required number of layers.

Orientation

Verify vertical/horizontal as specified.

Staggering

Check joints between layers where required.

Fasteners

Check:

- type;

- spacing;

- edge distance;

- proper set;

- no torn paper/overdriven screws beyond allowable condition.

Joints

Check:

- tight but appropriate;

- staggered;

- taped;

- compound applied correctly.

Perimeters/interfaces

Check:

- floor;

- ceiling;

- columns;

- door frames;

- penetrations;

- fire/acoustic sealants.

6.4.6 RECORDS / EVIDENCE

Capture:

- wall/room;

- board type;

- layers;

- representative fastening;

- fire-rated conditions;

- moisture areas;

- defects;

- repairs.

6.4.7 NC / DEFICIENCY

Common:

- wrong board;

- missing layer;

- joints aligned improperly;

- wrong screw spacing;

- excessive gaps;

- damaged board;

- board installed before concealed-work acceptance;

- fire-rated assembly deviated from listed detail.

6.4.8 CORRECTIVE ACTION — EXAMPLE

Single layer installed where two layers required for fire-rated assembly.

Identify extent → compare approved assembly → control finish work → add/replace layers as required → verify fastener/joint pattern → reinspect → document.

6.4.9 VERIFICATION

Confirm:

- correct assembly restored;

- layers;

- fastening;

- joints;

- interfaces;

- fire/acoustic continuity.

6.4.10 CLOSURE

☐ correct board
☐ correct layers
☐ orientation correct
☐ fasteners accepted
☐ joints treated
☐ perimeters sealed
☐ fire/moisture requirements met
☐ ready for finish

6.4.11 REPORTING / ANALYSIS

Track:

- wrong board use;

- missing layers;

- recurring fastener defects;

- premature wall closure.

6.4.12 QUALITY CHECKPOINT

☐ Board type
☐ Thickness
☐ Layers
☐ Orientation
☐ Joint staggering
☐ Fasteners
☐ Joints
☐ Perimeters
☐ Fire/moisture conditions
☐ Closure evidence

6.5 FIRE-RATED ASSEMBLIES

This is a high-priority life-safety quality system.

Quality objective

Ensure every fire-rated wall, floor, ceiling, shaft and related assembly matches the approved/listed system and remains continuous at joints, openings, penetrations and interfaces.

The key principle is:

A fire-rated assembly is a system, not just a “fire-rated board.”

6.5.1 REQUIREMENTS

🔵 Obtain:

- code/life-safety plans;

- fire separation plans;

- wall/ceiling schedules;

- listed/tested assembly references;

- rated door schedules;

- firestopping details;

- head-of-wall systems;

- shaft systems;

- approved products;

- manufacturer/system listings;

- PIE/PRIE.

Extract:

- required rating;

- assembly ID;

- stud/masonry type;

- board layers;

- insulation;

- fasteners;

- joints;

- head-of-wall;

- penetrations;

- firestop system;

- door/frame rating.

6.5.2 PLANNING

Before construction:

- map rated walls/ceilings;

- identify penetrations;

- coordinate MEP;

- identify rated doors;

- establish pre-concealment inspection points;

- identify firestop documentation requirements.

6.5.3 DOCUMENT CONTROL

Verify:

☐ correct assembly ID
☐ current rated-wall plan
☐ tested/listed system
☐ current penetration details
☐ current firestop system
☐ rated door schedule

6.5.4 MATERIAL CONTROL

Check:

- studs/blocks;

- gypsum type;

- insulation;

- firestop;

- sealants;

- joint systems;

- doors/frames;

- dampers;

- product listings.

6.5.5 INSPECTION / TESTING

Check:

Assembly identification

Correct wall/ceiling at correct location.

Components

Correct:

- studs;

- board type;

- layers;

- insulation;

- joints.

Continuity

Inspect:

- floor-to-floor;

- wall-to-deck;

- columns;

- corners;

- intersections.

Penetrations

Every penetration must use an approved system compatible with:

- wall/floor type;

- penetrating item;

- opening size;

- required rating.

Openings

Check:

- doors;

- access panels;

- dampers;

- glazing where rated.

6.5.6 RECORDS / EVIDENCE

Capture:

- assembly ID;

- location;

- rated-wall map;

- pre-concealment photos;

- firestop IDs;

- product/system references;

- door/frame tags;

- deficiency records.

6.5.7 NC / DEFICIENCY

Common:

- wrong board layer;

- unsealed penetration;

- missing head-of-wall system;

- incompatible firestop;

- rated wall stops below deck improperly;

- non-rated access panel;

- wrong rated door/frame.

6.5.8 CORRECTIVE ACTION — EXAMPLE

Cable tray penetrates 2-hour wall with no completed firestop.

Identify penetration → hold concealment → confirm approved firestop system → install required backing/material/depth → label/document if required → inspect → photograph → close.

6.5.9 VERIFICATION

Confirm:

- system matches approved listing;

- depth/thickness correct;

- annular space acceptable;

- continuity restored;

- documentation complete.

6.5.10 CLOSURE

☐ rated assembly correct
☐ components complete
☐ continuity complete
☐ penetrations firestopped
☐ rated openings complete
☐ documentation complete
☐ deficiencies closed

6.5.11 REPORTING / ANALYSIS

Track:

- recurring unsealed penetrations;

- firestop rework;

- trade coordination problems;

- wrong rated components.

6.5.12 QUALITY CHECKPOINT

☐ Assembly ID
☐ Required rating
☐ Correct components
☐ Full continuity
☐ Head-of-wall
☐ Penetrations
☐ Openings
☐ Firestop system
☐ Rated doors/panels
☐ Documentation

6.6 INTERIOR DOORS & FRAMES

Quality objective

Install the correct door/frame assemblies in the correct openings, aligned and securely anchored, with proper clearances and compatibility with hardware, fire rating, access control and finishes.

6.6.1 REQUIREMENTS

Obtain:

- door schedule;

- frame schedule;

- hardware schedule;

- fire-rating requirements;

- opening details;

- wall types;

- approved shop drawings;

- access-control/security details;

- glazing details;

- manufacturer instructions;

- PIE/PRIE.

6.6.2 PLANNING

Before installation:

- verify opening size;

- wall thickness;

- floor finish elevation;

- frame type;

- fire rating;

- hardware prep;

- electrical access-control prep;

- sequence with drywall/masonry.

6.6.3 DOCUMENT CONTROL

Verify:

☐ correct door ID
☐ correct frame
☐ current hardware set
☐ fire rating
☐ opening dimensions
☐ access-control requirements

6.6.4 MATERIAL CONTROL

Check:

- door leaf;

- frame;

- finish;

- glazing;

- labels;

- anchors;

- hardware prep;

- fire labels;

- damage.

6.6.5 INSPECTION

Frame

Check:

- plumb;

- level;

- square;

- wall alignment;

- anchoring;

- throat size;

- head/jamb condition.

Door

Check:

- correct leaf;

- swing;

- handing;

- clearances;

- finish;

- damage.

Fire-rated units

Check:

- labels intact;

- compatible frame/door;

- glazing/hardware rated as required.

6.6.6 RECORDS

Capture:

- door ID;

- frame;

- fire label;

- alignment;

- damage;

- deficiencies.

6.6.7 NC / DEFICIENCY

Common:

- wrong swing;

- wrong frame;

- out-of-square;

- incorrect opening;

- damaged finish;

- missing fire label;

- hardware prep mismatch.

6.6.8 CORRECTIVE ACTION

Example:

Frame installed out of square causing door bind.

Measure → adjust/reinstall frame → verify wall finish not compromised → hang door → recheck clearances/operation → document closure.

6.6.9 VERIFICATION

Confirm:

- alignment;

- clearances;

- swing;

- labels;

- readiness for hardware.

6.6.10 CLOSURE

☐ correct door/frame
☐ frame aligned
☐ swing/handing correct
☐ clearances acceptable
☐ fire labels complete
☐ finish acceptable
☐ hardware-ready

6.6.11 REPORTING / ANALYSIS

Track recurring frame/opening or door-schedule discrepancies.

6.6.12 QUALITY CHECKPOINT

☐ Door ID
☐ Frame type
☐ Opening
☐ Alignment
☐ Anchoring
☐ Swing/handing
☐ Clearances
☐ Fire rating
☐ Finish
☐ Ready for hardware

6.7 DOOR HARDWARE

Quality objective

Install the specified hardware set completely and correctly so each door operates, latches, locks, closes and performs its fire/life-safety/security function as designed.

6.7.1 REQUIREMENTS

Obtain:

- hardware schedule;

- door schedule;

- approved hardware submittal;

- fire-rating requirements;

- accessibility requirements;

- access-control/security drawings;

- manufacturer instructions;

- electrified hardware requirements;

- PIE/PRIE.

Extract:

- hinges;

- locks;

- closers;

- panic hardware;

- coordinators;

- stops;

- seals;

- thresholds;

- kick plates;

- access-control devices.

6.7.2 PLANNING

Coordinate:

- hardware delivery;

- door/frame preparation;

- electrical rough-in;

- access-control programming;

- fire alarm interface where applicable;

- testing.

6.7.3 DOCUMENT CONTROL

Verify:

☐ correct hardware set
☐ correct door ID
☐ fire-rated requirements
☐ electrified hardware detail
☐ current access-control logic

6.7.4 MATERIAL CONTROL

Check:

- correct hardware;

- finish;

- ratings;

- labels;

- damage;

- fasteners;

- electrified components.

6.7.5 INSPECTION / TESTING

Check:

Hinges

- correct quantity/type;

- secure fastening;

- smooth operation.

Lock/latch

- correct hardware;

- latch engages;

- lock functions.

Closer

- securely installed;

- closes door;

- latches;

- adjusted appropriately.

Panic hardware

- operates;

- releases correctly.

Fire-rated doors

Verify:

- self-closing;

- positive latching;

- no unauthorized hold-open condition;

- seals as required.

Access control

Check physical interface with:

- strike;

- maglock;

- reader;

- door contact;

- release devices.

Actual functional testing should follow project procedure.

6.7.6 RECORDS

Capture:

- door ID;

- hardware set;

- functional test;

- deficiencies;

- corrective work.

6.7.7 NC / DEFICIENCY

Common:

- wrong hardware;

- missing hardware;

- door doesn't latch;

- closer improperly adjusted;

- panic device fails;

- access-control mismatch;

- fire door held open improperly.

6.7.8 CORRECTIVE ACTION — EXAMPLE

Rated door closes but does not latch.

Identify cause → frame alignment / strike / closer adjustment → correct → cycle-test door repeatedly → confirm positive latch → document closure.

6.7.9 VERIFICATION

Function-test corrected door.

6.7.10 CLOSURE

☐ complete hardware set
☐ door operates
☐ closes
☐ latches
☐ locks
☐ fire/life safety functions
☐ access-control interface complete

6.7.11 REPORTING / ANALYSIS

Track recurring:

- closer issues;

- hardware schedule errors;

- electrified hardware coordination;

- fire-door failures.

6.7.12 QUALITY CHECKPOINT

☐ Hardware set complete
☐ Hinges
☐ Lock/latch
☐ Closer
☐ Panic device
☐ Stops/seals
☐ Access control
☐ Fire function
☐ Operation test

6.8 CEILINGS

Quality objective

Install suspended or panel ceiling systems at the correct elevation and alignment, securely supported, coordinated with MEP devices, and complete with required access and fire/acoustic features.

6.8.1 REQUIREMENTS

Obtain:

- reflected ceiling plans;

- ceiling schedules;

- suspension details;

- seismic/bracing requirements if applicable;

- fire-rated ceiling details;

- ceiling specifications;

- tile/panel approvals;

- MEP coordination drawings;

- lighting/device layouts;

- access-panel requirements;

- manufacturer instructions;

- PIE/PRIE.

6.8.2 PLANNING

Before ceiling closure:

- overhead MEP substantially complete;

- required tests complete;

- firestopping complete;

- insulation complete;

- access requirements identified;

- ceiling devices coordinated;

- inspection above ceiling performed.

This is another major pre-concealment gate.

6.8.3 DOCUMENT CONTROL

Verify:

☐ correct ceiling type
☐ current RCP
☐ grid layout
☐ elevation
☐ light/device layout
☐ access-panel locations
☐ fire-rated requirements

6.8.4 MATERIAL CONTROL

Check:

- grid;

- hangers;

- wires/rods;

- tiles/panels;

- perimeter trims;

- seismic clips/bracing where required;

- access panels.

6.8.5 INSPECTION / TESTING

Suspension

Check:

- hangers;

- spacing;

- attachment;

- independent support;

- no inappropriate support from MEP.

Grid

Check:

- level;

- alignment;

- module size;

- perimeter support.

Tiles/panels

Check:

- correct type;

- finish;

- fit;

- damage;

- orientation.

Coordination with MEP

Check:

- lights;

- diffusers;

- sprinklers;

- detectors;

- speakers;

- access panels;

- no clashes.

Access

Verify:

- equipment requiring service is accessible;

- valves/dampers/junction boxes not permanently hidden if access is required.

6.8.6 RECORDS

Capture:

- ceiling zone;

- above-ceiling inspection;

- grid/suspension;

- coordinated devices;

- access-panel locations;

- final appearance.

6.8.7 NC / DEFICIENCY

Common:

- ceiling wrong elevation;

- unsupported grid;

- poor alignment;

- damaged tiles;

- device clashes;

- hidden equipment without access;

- grid supported from duct/pipe.

6.8.8 CORRECTIVE ACTION — EXAMPLE

Control valve becomes inaccessible after ceiling tile layout.

Identify equipment/access requirement → coordinate access-panel location → install approved panel → verify usability → update record/as-built if required.

6.8.9 VERIFICATION

Confirm:

- ceiling level;

- grid secure;

- access available;

- devices aligned;

- damaged panels replaced.

6.8.10 CLOSURE

☐ above-ceiling work accepted
☐ suspension accepted
☐ grid accepted
☐ panels accepted
☐ MEP coordination complete
☐ access provided
☐ final appearance accepted

6.8.11 REPORTING / ANALYSIS

Track recurring:

- access issues;

- device misalignment;

- grid support defects;

- damaged tiles.

6.8.12 QUALITY CHECKPOINT

☐ Above-ceiling inspection
☐ Suspension
☐ Grid
☐ Elevation
☐ Tiles/panels
☐ Lights
☐ Diffusers
☐ Sprinklers/detectors
☐ Access panels
☐ Final appearance

6.9 ACCESS PANELS

Quality objective

Provide correctly sized, located and rated access panels wherever concealed equipment, valves, dampers, controls or other maintainable components require future access.

6.9.1 REQUIREMENTS

Obtain:

- architectural drawings;

- reflected ceiling plans;

- mechanical/electrical drawings;

- equipment access requirements;

- access-panel schedule;

- fire-rated panel requirements;

- approved product data;

- manufacturer instructions.

6.9.2 PLANNING

Before walls/ceilings close:

- identify all concealed maintainable items;

- map required access;

- coordinate panel location with finishes;

- verify size and rating.

6.9.3 DOCUMENT CONTROL

Verify:

☐ correct location
☐ correct panel size
☐ required fire rating
☐ correct finish
☐ current service/equipment location

6.9.4 MATERIAL CONTROL

Check:

- panel type;

- size;

- frame;

- latch;

- rating;

- finish;

- hardware.

6.9.5 INSPECTION

Check:

- location;

- clear opening;

- alignment;

- anchorage;

- door operation;

- access to actual service;

- fire rating where applicable;

- finish integration.

The key test:

Can a technician actually reach, inspect, operate and maintain the hidden item through this panel?

6.9.6 RECORDS

Capture:

- panel ID/location;

- equipment served;

- panel type/rating;

- photo;

- deficiency/correction.

6.9.7 NC / DEFICIENCY

Common:

- missing panel;

- panel too small;

- panel misaligned from valve/equipment;

- non-rated panel in rated wall;

- panel obstructed;

- poor finish.

6.9.8 CORRECTIVE ACTION — EXAMPLE

Panel installed 400 mm away from the valve it is supposed to serve.

Verify valve location → determine practical/approved access point → relocate/enlarge panel → repair wall finish → verify actual access → document.

6.9.9 VERIFICATION

Physically open panel and verify serviceability.

6.9.10 CLOSURE

☐ correct panel
☐ correct location
☐ correct size
☐ correct rating
☐ actual access achieved
☐ operation accepted
☐ finish accepted

6.9.11 REPORTING / ANALYSIS

Track recurring access-coordination problems, because these usually reveal poor architectural/MEP coordination rather than isolated panel workmanship.

6.9.12 QUALITY CHECKPOINT

☐ Equipment requiring access identified
☐ Panel provided
☐ Correct size
☐ Correct location
☐ Rating correct
☐ Anchoring
☐ Operation
☐ Actual maintainability
☐ Finish complete

INTERIOR ARCHITECTURAL — MASTER PRE-CONCEALMENT GATE

Before closing a wall or ceiling, your system should force a final review.

DOCUMENTS

☐ Current wall/ceiling type
☐ Current MEP drawings
☐ Current fire/life-safety details
☐ Latest technical changes

FRAMING / MASONRY

☐ Layout correct
☐ Openings correct
☐ Backing complete
☐ Reinforcement complete
☐ Anchors/support complete

MEP

☐ Rough-in complete
☐ Required tests complete
☐ Boxes/sleeves correct
☐ Services supported
☐ No unresolved clashes

FIRE / ACOUSTIC

☐ Rated assembly correct
☐ Firestopping complete where required
☐ Acoustic insulation complete
☐ Head-of-wall complete
☐ Rated openings coordinated

ACCESS

☐ Valves accessible
☐ Dampers accessible
☐ Junction boxes/access-required items addressed
☐ Access panels identified

EVIDENCE

☐ Pre-concealment photographs
☐ Inspection records
☐ Test records
☐ Deficiencies corrected
☐ Release obtained where required

Only then:

WALL/CEILING READY TO CLOSE

PRACTICAL EXAMPLE — FIRE-RATED STUD WALL WITH MEP SERVICES

Suppose tomorrow they want to close one side of a 2-hour rated wall.

You don't just inspect drywall.

You open:

Interior Construction → Metal Stud Framing
then
Interior Insulation
then
Fire-Rated Assemblies

and cross-reference MEP penetrations.

Your sequence becomes:

1. Requirements

Find:

- wall type;

- required rating;

- approved listed assembly;

- stud gauge/spacing;

- board layers;

- insulation;

- head-of-wall detail;

- penetration/firestop requirements.

2. Framing

Check:

- studs;

- spacing;

- track;

- head condition;

- openings;

- backing.

3. MEP rough-in

Check:

- conduits;

- pipes;

- boxes;

- openings;

- no unauthorized cuts.

4. Insulation

Check full cavity where required.

5. Fire integrity

Identify every penetration.

Ask:

Does each one have a valid path to a compliant firestop system before closure?

6. Evidence

Take:

- overall wall photo;

- framing;

- insulation;

- penetrations;

- head-of-wall;

- critical details.

7. Close wall

Only after all required pre-concealment items are accepted.

That is much stronger than arriving after gypsum is installed and asking:

“Did they put the right insulation behind there?” 😂

BUILD 2 — INTERIOR ARCHITECTURAL STATUS

6.1 Interior Masonry ✓
6.2 Metal Stud Framing ✓
6.3 Interior Insulation ✓
6.4 Gypsum Board ✓
6.5 Fire-Rated Assemblies ✓
6.6 Interior Doors & Frames ✓
6.7 Door Hardware ✓
6.8 Ceilings ✓
6.9 Access Panels ✓

Perfect. We’ll keep the exact same execution model.

For Finishes, the quality objective shifts. Structural and envelope work is mostly about hidden technical compliance and performance. Finishes are more sensitive to:

substrate readiness → environmental conditions → approved material/system → installation workmanship → visual uniformity → protection → final deficiency closure.

The governing rule remains:

CRT/Hydro-Québec drawings, devis, Plan Qualité, PIE/PRIE, approved samples/mock-ups, manufacturer instructions, technical data sheets, colour/finish schedules, and applicable project standards govern.

7. FINISHES

7.1 CONCRETE FLOOR PREPARATION

Quality objective

Provide a clean, sound, dry, level, properly profiled concrete substrate suitable for the specified floor finish system.

A large percentage of floor-finish failures originate in poor substrate preparation rather than the finish material itself.

7.1.1 Requirements — where to get them

🔵 Obtain:

- finish schedule;

- floor finish drawings;

- concrete slab drawings;

- floor-finish specifications;

- substrate preparation requirements;

- manufacturer instructions;

- moisture limits;

- surface-profile requirements;

- flatness/levelness tolerances where applicable;

- crack/joint treatment details;

- primers/patching systems;

- approved product data;

- PIE/PRIE;

- technical changes.

Extract:

- required substrate condition;

- moisture criterion;

- surface profile;

- flatness/levelness;

- minimum curing age if specified;

- crack treatment;

- joint treatment;

- contaminant-removal requirements;

- approved levelling/patching products.

7.1.2 Planning

Before finish installation:

- confirm slab sufficiently cured;

- identify finish type by room/zone;

- identify moisture testing requirement;

- identify levelness/flatness criteria;

- coordinate grinding/shot blasting/scarifying where needed;

- locate cracks, joints, spalls, laitance;

- identify contamination;

- confirm HVAC/environmental conditions if required.

7.1.3 Document control

Verify:

☐ correct finish type
☐ current finish schedule
☐ current floor elevations
☐ approved preparation method
☐ approved repair/patch products
☐ current moisture requirement
☐ latest technical changes

7.1.4 Material control

Check:

- patching material;

- levelling compound;

- primer;

- crack-repair product;

- moisture mitigation system if specified;

- shelf life;

- compatibility;

- storage.

7.1.5 Inspection / testing

Check:

Surface condition

- dust;

- dirt;

- grease/oil;

- laitance;

- curing compounds;

- loose material;

- paint/contaminants.

Soundness

- cracks;

- spalls;

- hollow/weak areas;

- delamination.

Flatness/levelness

Verify where specified.

Moisture

Perform/review required test method.

Surface profile

Confirm preparation method achieves required texture/profile.

Joints/cracks

Verify:

- movement joints respected;

- cracks treated per approved method;

- patching flush and sound.

7.1.6 Records / evidence

Capture:

- room/zone;

- floor-finish type;

- moisture-test results;

- substrate photos;

- crack/joint map;

- repair locations;

- flatness/levelness records;

- primer/patch product;

- acceptance status.

7.1.7 NC / deficiency

Common:

- excessive moisture;

- contaminated slab;

- poor profile;

- cracks untreated;

- high/low spots;

- loose patch;

- floor finish installed before substrate acceptance.

7.1.8 Corrective action — example

Moisture test exceeds finish-system limit.

Identify area → confirm test validity → compare to manufacturer/project criteria → hold finish installation → obtain approved mitigation/drying approach → retest → document result → release.

7.1.9 Verification

Confirm:

- repaired substrate;

- moisture acceptable;

- surface profile correct;

- patching sound;

- elevations acceptable.

7.1.10 Closure

☐ substrate clean
☐ sound
☐ dry within limits
☐ correct profile
☐ level/flat enough
☐ cracks/joints treated
☐ repairs accepted
☐ ready for finish

7.1.11 Reporting / analysis

Track:

- recurring moisture failures;

- slab cracking;

- patching issues;

- local levelness problems;

- delayed finish installation.

7.1.12 Quality checkpoint

☐ Correct finish zone
☐ Moisture checked
☐ Surface clean
☐ Profile acceptable
☐ Cracks treated
☐ Joints addressed
☐ Flatness/levelness verified
☐ Repairs complete
☐ Ready for flooring

7.2 FLOOR FINISHES

This module should branch by system because tile, resilient flooring and epoxy behave very differently.

7.2.1 TILE

Quality objective

Install tile with the correct product, layout, substrate preparation, bonding coverage, alignment, joint spacing, movement joints and finish.

Requirements

Obtain:

- finish schedule;

- tile layout;

- tile specification;

- approved samples;

- adhesive/mortar;

- grout;

- movement-joint details;

- waterproofing details where applicable;

- manufacturer instructions;

- PIE/PRIE.

Planning

- verify substrate accepted;

- establish layout/grid;

- coordinate cuts;

- identify drains;

- verify slopes in wet areas;

- establish expansion/movement joints;

- coordinate wall/floor transitions.

Material control

Check:

- tile type;

- size;

- colour;

- batch/lot consistency;

- damaged units;

- adhesive/mortar;

- grout;

- spacers;

- transition profiles.

Inspection

Check:

- layout;

- alignment;

- joint width;

- lippage;

- cut quality;

- bonding;

- coverage where required;

- slope;

- perimeter joints;

- movement joints;

- grout;

- hollow/loose tiles.

Records

Capture:

- room;

- approved tile;

- layout;

- mock-up/reference;

- slope;

- defects;

- corrective work.

Common deficiencies

- poor alignment;

- inconsistent joints;

- lippage;

- hollow tiles;

- wrong tile;

- chipped edges;

- incorrect slope;

- missing movement joints.

Corrective example

Tile floor around drain does not maintain required slope.

Measure slope → identify affected area → remove/rebuild substrate or tile as approved → reinstall → verify drainage → document.

Closure

☐ correct tile
☐ layout accepted
☐ alignment accepted
☐ joints consistent
☐ slope correct
☐ movement joints complete
☐ grout complete
☐ damaged/hollow tiles corrected

7.2.2 RESILIENT FLOORING

Quality objective

Install resilient flooring over a properly prepared, dry, smooth substrate with correct adhesive, seams, layout and transitions.

Requirements

Obtain:

- finish schedule;

- flooring specification;

- approved product;

- manufacturer instructions;

- moisture limits;

- adhesive;

- seam treatment;

- cove base/transition details.

Planning

- substrate accepted;

- environmental conditioning;

- material acclimatization if required;

- layout;

- seams;

- transitions;

- room sequence.

Material control

Check:

- product;

- colour/pattern;

- lot consistency;

- adhesive;

- shelf life;

- storage;

- damaged rolls/tiles.

Inspection

Check:

- substrate smoothness;

- adhesive coverage;

- correct open time where specified;

- layout;

- seams;

- bubbles;

- wrinkles;

- edge bonding;

- transitions;

- cove base;

- damage.

Deficiencies

- bubbles;

- lifting edges;

- seam opening;

- telegraphing substrate defects;

- colour mismatch;

- adhesive failure.

Corrective example

Vinyl flooring develops bubbles after installation.

Identify extent → verify substrate moisture/adhesive condition → determine approved repair → lift/rebond or replace as required → reinspect → document.

Closure

☐ substrate accepted
☐ correct material
☐ adhesive correct
☐ seams accepted
☐ no bubbles/lifting
☐ transitions complete
☐ protection applied

7.2.3 EPOXY / FLOOR COATINGS

Quality objective

Apply the approved floor-coating system to a properly prepared substrate under acceptable environmental conditions at the required thickness and finish.

Requirements

Obtain:

- coating specification;

- approved system;

- surface-profile requirement;

- moisture limit;

- temperature/humidity limits;

- primer;

- coat sequence;

- DFT/WFT requirements where applicable;

- curing times;

- slip-resistance requirements.

Planning

- isolate area;

- substrate testing;

- environmental monitoring;

- ventilation;

- cure time;

- traffic protection.

Material control

Check:

- batch;

- mix ratio;

- shelf life;

- colour;

- primer;

- aggregate;

- compatible products.

Inspection

Check:

- substrate prep;

- mixing;

- pot life;

- application;

- thickness;

- coverage;

- pinholes;

- bubbles;

- delamination;

- colour consistency;

- texture;

- curing.

Records

Capture:

- area;

- batch;

- environmental conditions;

- surface prep;

- thickness;

- cure;

- defects.

Deficiencies

- poor adhesion;

- pinholes;

- blistering;

- thin spots;

- colour variation;

- premature traffic damage.

Corrective example

Coating pulls off during adhesion check.

Identify failed area → verify surface preparation/moisture → remove unsound coating → reprepare → reapply approved system → retest → close.

7.3 WALL FINISHES

Quality objective

Provide wall finishes that are installed over suitable substrates, use approved materials, follow required alignment/layout and achieve the specified appearance and durability.

This can include:

- wall tile;

- panels;

- acoustic panels;

- wall protection;

- laminates;

- specialty wall systems.

7.3.1 Requirements

Obtain:

- finish schedule;

- elevations;

- finish details;

- approved samples/mock-ups;

- substrate requirements;

- adhesives/fasteners;

- joint details;

- manufacturer instructions;

- fire-performance requirements where applicable.

7.3.2 Planning

- substrate accepted;

- layout established;

- openings/MEP devices coordinated;

- corners/transitions planned;

- mock-up approved;

- protection after installation planned.

7.3.3 Document control

Verify:

☐ correct finish by room/elevation
☐ current colour/pattern
☐ approved layout
☐ current transitions/edge details
☐ approved product

7.3.4 Material control

Check:

- finish product;

- colour;

- lot/batch;

- damage;

- adhesive;

- trims;

- fasteners;

- accessories.

7.3.5 Inspection

Check:

- substrate;

- alignment;

- pattern;

- joints;

- edges;

- corners;

- fastening;

- adhesive;

- penetrations;

- transitions;

- finish consistency;

- damage.

7.3.6 Records

Capture:

- room/elevation;

- finish type;

- approved sample reference;

- layout;

- defects;

- corrections.

7.3.7 NC / deficiency

Common:

- wrong finish;

- poor alignment;

- visible gaps;

- damaged panels;

- mismatched colour;

- poor edge treatment;

- loose adhesion.

7.3.8 Corrective action

Remove/replace/adjust affected finish per approved method.

7.3.9 Verification

Compare corrected area to approved sample/mock-up.

7.3.10 Closure

☐ correct finish
☐ layout accepted
☐ edges/joints correct
☐ attachment accepted
☐ appearance accepted
☐ protected

7.3.11 Reporting / analysis

Track recurring damage, layout inconsistency or batch mismatch.

7.3.12 Quality checkpoint

☐ Product
☐ Colour/pattern
☐ Substrate
☐ Layout
☐ Joints
☐ Edges/corners
☐ Penetrations
☐ Attachment
☐ Appearance
☐ Protection

7.4 PAINTING / COATINGS

Quality objective

Apply the specified coating system to a properly prepared substrate under acceptable conditions, with correct coverage, thickness, curing and uniform final appearance.

7.4.1 Requirements

🔵 Obtain:

- finish schedule;

- paint/coating specification;

- approved colours;

- approved manufacturer/system;

- substrate preparation;

- primer requirements;

- number of coats;

- DFT/WFT requirements where specified;

- environmental limitations;

- curing times;

- mock-up requirements;

- PIE/PRIE.

7.4.2 Planning

Before painting:

- substrate complete;

- repairs complete;

- moisture acceptable;

- room/environment suitable;

- adjacent work protected;

- colour schedule confirmed;

- coating sequence established.

7.4.3 Document control

Verify:

☐ correct room/zone
☐ correct colour
☐ correct coating system
☐ correct primer
☐ correct coat count
☐ current finish schedule

7.4.4 Material control

Check:

- paint/coating;

- colour code;

- batch;

- shelf life;

- primer;

- thinner if permitted;

- storage;

- mixing requirements.

7.4.5 Inspection / testing

Surface preparation

Check:

- clean;

- dry;

- smooth;

- patched;

- sanded;

- free of dust;

- existing coating compatible.

Environmental conditions

Monitor where required:

- temperature;

- humidity;

- dew point;

- ventilation.

Application

Check:

- primer;

- number of coats;

- uniform coverage;

- recoat time;

- application method.

Thickness

Where specified:

- wet film thickness;

- dry film thickness.

Finish

Look for:

- runs;

- sags;

- holidays;

- pinholes;

- brush/roller marks;

- overspray;

- colour variation;

- poor coverage;

- contamination.

7.4.6 Records

Capture:

- room/zone;

- product;

- colour;

- batch;

- environmental conditions;

- coat sequence;

- thickness records;

- defects;

- repairs.

7.4.7 NC / deficiency

Common:

- wrong colour;

- wrong product;

- missed primer;

- insufficient coats;

- thin coating;

- runs/sags;

- poor substrate prep;

- coating over damp surface.

7.4.8 Corrective action — example

DFT readings below specification on steel/painted surface.

Map deficient area → confirm required DFT → prepare surface if necessary → apply additional coat → remeasure → document accepted results.

7.4.9 Verification

Confirm:

- required thickness;

- uniform colour;

- defects repaired;

- complete curing.

7.4.10 Closure

☐ substrate accepted
☐ primer complete
☐ coat sequence complete
☐ thickness accepted
☐ colour correct
☐ appearance accepted
☐ damage repaired

7.4.11 Reporting / analysis

Track:

- recurring thin spots;

- surface-prep failures;

- colour mismatch;

- environmental-condition issues.

7.4.12 Quality checkpoint

☐ Surface prep
☐ Product
☐ Colour
☐ Primer
☐ Environmental conditions
☐ Coat count
☐ Thickness
☐ Coverage
☐ Finish
☐ Cure
☐ Repairs

7.5 ARCHITECTURAL SEALANTS

This differs slightly from exterior-envelope sealants because interior architectural sealants may be used for:

- acoustic control;

- sanitary joints;

- finish joints;

- movement joints;

- perimeter sealing.

Quality objective

Install compatible sealant systems with correct joint preparation, geometry, adhesion and finish while maintaining the intended acoustic, sanitary or movement function.

7.5.1 Requirements

Obtain:

- architectural details;

- sealant specification;

- approved product;

- joint type;

- colour;

- primer;

- backer rod;

- movement requirement;

- sanitary/acoustic requirements;

- manufacturer instructions.

7.5.2 Planning

Identify:

- joint locations;

- substrate compatibility;

- sequencing;

- environmental conditions;

- finish requirements.

7.5.3 Document control

Verify:

☐ correct sealant for application
☐ colour
☐ joint geometry
☐ primer/backer rod
☐ technical details

7.5.4 Material control

Check:

- sealant;

- batch;

- shelf life;

- colour;

- primer;

- backer rod;

- cleaner.

7.5.5 Inspection

Check:

- clean joint;

- correct depth/width;

- backer rod;

- primer;

- continuous application;

- full adhesion;

- no voids;

- tooling;

- clean edges.

7.5.6 Records

Capture representative critical joints and defects.

7.5.7 NC / deficiency

Common:

- wrong sealant;

- missing backer rod;

- poor adhesion;

- gaps;

- wrong colour;

- excessive smearing;

- missing joint.

7.5.8 Corrective action

Remove failed sealant, prepare joint correctly, reinstall, reinspect.

7.5.9 Verification

Check adhesion and final appearance.

7.5.10 Closure

☐ correct product
☐ joint prep correct
☐ geometry correct
☐ adhesion accepted
☐ appearance accepted

7.5.11 Reporting / analysis

Trend recurring adhesion/workmanship issues.

7.5.12 Quality checkpoint

☐ Product
☐ Colour
☐ Joint prep
☐ Backer rod
☐ Primer
☐ Application
☐ Adhesion
☐ Tooling
☐ Appearance

7.6 SPECIALTY FINISHES

This is intentionally flexible because Hochelaga may include systems we haven't yet seen.

Examples:

- epoxy wall systems;

- protective wall panels;

- FRP panels;

- acoustic treatments;

- anti-static flooring;

- industrial coatings;

- specialty ceiling/wall systems.

Quality objective

Ensure specialty finishes are installed from approved products and mock-ups using the manufacturer/project-defined substrate preparation, sequencing and inspection criteria.

7.6.1 Requirements

Obtain:

- specialty finish specification;

- approved submittal;

- shop drawings;

- manufacturer instructions;

- mock-up/sample;

- substrate criteria;

- adhesive/fastener system;

- environmental limits;

- testing requirements.

7.6.2 Planning

Identify:

- substrate readiness;

- environmental needs;

- mock-up/reference standard;

- skilled installer requirements;

- sequence;

- protection.

7.6.3 Document control

Verify latest approved:

- product;

- details;

- manufacturer requirements;

- finish/pattern.

7.6.4 Material control

Check:

- product;

- batch;

- colour;

- accessories;

- adhesives;

- fasteners;

- condition;

- storage.

7.6.5 Inspection

Check:

- substrate;

- layout;

- installation method;

- fastening/adhesion;

- seams/joints;

- edges;

- finish;

- compatibility;

- protection.

7.6.6 Records

Capture:

- system;

- location;

- product;

- mock-up reference;

- installation;

- deficiencies.

7.6.7 NC / deficiency

Any deviation from:

- approved system;

- layout;

- substrate requirement;

- attachment;

- manufacturer instruction.

7.6.8 Corrective action

Follow approved manufacturer/project repair method.

7.6.9 Verification

Compare repaired work to approved mock-up/sample.

7.6.10 Closure

☐ approved system
☐ substrate accepted
☐ installation accepted
☐ appearance accepted
☐ protection complete

7.6.11 Reporting / analysis

Track recurring installer/product issues.

7.6.12 Quality checkpoint

☐ Product
☐ Substrate
☐ Mock-up/reference
☐ Layout
☐ Installation
☐ Attachment
☐ Finish
☐ Protection

7.7 FINAL ARCHITECTURAL DEFICIENCY INSPECTION

This is where all interior architectural quality streams converge.

Quality objective

Identify, document, assign, verify and close all architectural deficiencies systematically before turnover, leaving no unresolved condition hidden in vague punch-list language.

7.7.1 Requirements

Obtain:

- architectural drawings;

- finish schedule;

- room data sheets if applicable;

- door/hardware schedule;

- reflected ceiling plans;

- approved samples/mock-ups;

- commissioning/turnover requirements;

- deficiency process;

- acceptance criteria;

- PIE/PRIE;

- client/Hydro-Québec turnover expectations.

7.7.2 Planning

Organize inspection by:

building → floor/zone → room → system

rather than wandering randomly.

For each room, follow a fixed path:

Ceiling → walls → doors → hardware → floors → sealants → equipment interfaces → final cleanliness

That prevents omissions.

7.7.3 Document control

Verify latest:

☐ room configuration
☐ finish schedule
☐ door/hardware schedule
☐ ceiling layout
☐ approved changes
☐ prior deficiency list

7.7.4 Material control

Mostly verification of final installed product:

- correct finish;

- colour;

- hardware;

- panels;

- tiles;

- accessories.

7.7.5 Inspection / testing

A. Ceiling

Check:

- grid/panels;

- alignment;

- stains/damage;

- access panels;

- device coordination.

B. Walls

Check:

- paint;

- drywall;

- joints;

- cracks;

- finish consistency;

- wall panels;

- sealants.

C. Doors

Check:

- frame;

- leaf;

- clearances;

- hardware;

- operation;

- finish;

- fire labels.

D. Floors

Check:

- damage;

- alignment;

- loose tile;

- seams;

- coating;

- transitions;

- cleanliness.

E. Sealants

Check:

- complete;

- bonded;

- clean.

F. Accessories / specialty items

Check:

- installed;

- aligned;

- secure;

- functional.

G. Interfaces

Check:

- gaps around MEP devices;

- unfinished penetrations;

- missing escutcheons;

- access panels;

- service clearances.

Functional checks

Where applicable:

- doors operate;

- access panels open;

- removable ceiling tiles accessible;

- no finishes obstruct equipment access.

7.7.6 RECORDS / OBJECTIVE EVIDENCE

Every deficiency should include:

- unique ID;

- exact location;

- room/zone;

- trade/system;

- concise description;

- requirement/reference where needed;

- photograph;

- responsible party;

- date identified;

- target date;

- status;

- correction evidence;

- reinspection date;

- closure.

Weak deficiency

“Fix wall.”

Strong deficiency

Room 102, north wall adjacent Door D102: approximately 300 mm vertical paint/gypsum finish damage at jamb transition; repair substrate and restore finish to match approved wall finish.

That is actionable.

7.7.7 NC / DEFICIENCY

At this stage, most items are likely deficiencies, but significant departures from requirements may still follow formal NCR procedures according to CRT's system.

Do not assume punch-list status automatically downgrades a serious non-conformance.

7.7.8 CORRECTIVE ACTION

The workflow:

Identify → assign → correct → photograph/record → reinspect → accept/reject → close

Do not close because the contractor says:

“Done.”

Close because you verified it.

7.7.9 VERIFICATION

For every item:

- revisit exact location;

- compare correction to requirement;

- check repair didn't create adjacent damage;

- retest function where applicable;

- update status.

Possible statuses:

OPEN → IN PROGRESS → READY FOR REINSPECTION → CLOSED

Use CRT's actual terminology once known.

7.7.10 CLOSURE

A room/zone closes when:

☐ architectural finishes complete
☐ doors/hardware functional
☐ ceilings complete
☐ floors complete
☐ sealants complete
☐ accessories complete
☐ visible defects corrected
☐ access maintained
☐ cleaning acceptable
☐ all deficiencies verified closed

7.7.11 REPORTING / ANALYSIS

This is where your management mindset matters.

Track:

- number of open deficiencies;

- responsible subcontractor;

- aging;

- closure rate;

- repeated defect types;

- repeated room/system issue;

- items blocking turnover.

Example:

If 18 doors have the same frame/closer defect, that's no longer just 18 punch-list items.

It's a systemic installation problem.

Escalate the pattern so the trade corrects the process, not merely each individual door.

7.7.12 FINAL ARCHITECTURAL QUALITY CHECKPOINT

CEILINGS

☐ Complete
☐ Level/aligned
☐ No damage/staining
☐ Access panels installed
☐ MEP devices coordinated

WALLS

☐ Finish complete
☐ No cracks/damage
☐ Colours correct
☐ Joints acceptable
☐ Sealants complete

FLOORS

☐ Correct finish
☐ No damage
☐ Joints/seams complete
☐ Slopes where required
☐ Transitions complete

DOORS

☐ Correct door
☐ Frame aligned
☐ Hardware complete
☐ Operates
☐ Latches/locks
☐ Fire requirements where applicable

DETAILS

☐ Sealants
☐ Trim
☐ Panels
☐ Accessories
☐ Penetrations finished
☐ Escutcheons/covers

FUNCTIONAL

☐ Access panels usable
☐ Doors usable
☐ Equipment access maintained
☐ No finish obstructs systems

DOCUMENTATION

☐ Deficiencies logged
☐ Responsible parties assigned
☐ Corrections documented
☐ Reinspection performed
☐ All items closed

FINISHES — MASTER QUALITY GATE

Before an area is considered architecturally finished:

SUBSTRATES

☐ Dry
☐ Clean
☐ Sound
☐ Properly prepared

MATERIALS

☐ Approved
☐ Correct colour/type
☐ Lot/batch consistency where relevant
☐ Undamaged

INSTALLATION

☐ Correct system
☐ Correct layout
☐ Correct thickness/layers
☐ Joints/transitions correct
☐ Appearance acceptable

ENVIRONMENT

☐ Temperature/humidity acceptable where required
☐ Cure times respected

PROTECTION

☐ Finished work protected from subsequent trades
☐ Damage prevented/controlled

FINAL

☐ Deficiency inspection complete
☐ Corrective work complete
☐ Reinspection complete
☐ Documentation complete
☐ Area accepted

PRACTICAL EXAMPLE — FLOOR FINISH IN AN ELECTRICAL ROOM

Suppose epoxy floor coating is scheduled tomorrow.

You should not simply arrive when they're already rolling coating.

Open:

Finishes → Concrete Floor Preparation
then
Finishes → Floor Finishes → Epoxy/Coatings

Your workflow:

Before application

Review:

- finish schedule;

- approved coating system;

- substrate profile;

- moisture limit;

- environmental limits;

- required thickness.

Inspect:

- slab moisture;

- cracks;

- contamination;

- surface profile;

- patching;

- drains/penetrations.

If substrate fails, coating doesn't start.

During application

Verify:

- primer;

- mixing;

- batch;

- pot life;

- environmental conditions;

- coat sequence;

- thickness where specified.

After application

Inspect:

- coverage;

- bubbles;

- pinholes;

- colour;

- cure;

- damage.

Then:

Protect it.

Because an otherwise perfect epoxy floor can be destroyed by another trade dragging equipment across it before cure.

That last step—protection of accepted finished work—is particularly important in this phase.

BUILD 2 — FINISHES STATUS

7.1 Concrete Floor Preparation ✓
7.2 Floor Finishes ✓
7.3 Wall Finishes ✓
7.4 Painting/Coatings ✓
7.5 Architectural Sealants ✓
7.6 Specialty Finishes ✓
7.7 Final Architectural Deficiency Inspection ✓

Absolutely. Mechanical Services needs to be one of the most structured parts of the playbook, because the quality risk is rarely just “is the pipe there?” It is usually about:

approved material → correct routing → supports → slopes → joints → penetrations → valves → insulation → testing → identification → accessibility → commissioning readiness

And for your role, one distinction must remain explicit:

You can inspect installation quality, conformity, documentation, approved materials, routing, supports, penetrations, access, test evidence, and closure.

You should not independently make engineering-design judgments outside your authority. Where acceptance depends on mechanical design criteria, specialized calculations, balancing results, equipment performance, or professional interpretation, verify against the approved documents and escalate to the Responsable qualité / mechanical professional as required.

8. MECHANICAL SERVICES

The overall quality objective is:

Ensure mechanical systems are built from approved materials and equipment, installed in the correct location and configuration, properly supported and accessible, tested as required, protected from damage, fully documented, and ready for commissioning and operation.

The universal mechanical workflow is:

Approved system → routing/layout → material/equipment verification → installation → supports → penetrations → testing → insulation → identification → commissioning interface → closure

8.1 PLUMBING — DOMESTIC WATER

Quality objective

Install the approved domestic-water system using the correct piping, fittings, valves and supports, with proper routing, jointing, testing, insulation and identification, without compromising accessibility or adjacent construction.

8.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- mechanical/plumbing plans;

- riser diagrams;

- plumbing schematics;

- equipment/plumbing schedules;

- piping specifications;

- approved shop drawings;

- approved material submittals;

- valve schedules;

- hanger/support details;

- insulation specifications;

- penetration/firestop details;

- testing/disinfection requirements;

- Plan Qualité;

- applicable PIE/PRIE;

- manufacturer instructions;

- technical directives;

- QMT/RFI responses.

Extract:

- pipe material;

- pipe size;

- routing;

- elevation where relevant;

- valves;

- joints;

- support spacing;

- penetration requirements;

- insulation;

- identification;

- test pressure/duration;

- flushing/disinfection where specified.

8.1.2 PLANNING

Before installation:

- identify zone/system;

- confirm approved piping material;

- review coordination drawings;

- identify congested areas;

- identify wall/floor penetrations;

- coordinate supports;

- identify concealed piping;

- identify test boundaries;

- schedule testing before insulation/concealment;

- verify valve access.

Critical question:

What part of this system will become impossible to inspect once walls/ceilings close?

8.1.3 DOCUMENT CONTROL

Verify:

☐ latest plumbing drawing
☐ latest riser/schematic
☐ approved material submittal
☐ current valve schedule
☐ current support details
☐ current firestop/penetration detail
☐ latest technical changes
☐ current test procedure

8.1.4 MATERIAL CONTROL

Check:

- pipe material;

- diameter;

- schedule/class/type;

- fittings;

- valves;

- unions/couplings;

- hangers/supports;

- insulation;

- identification materials;

- manufacturer;

- certifications where required;

- damaged/contaminated material.

8.1.5 INSPECTION / TESTING

Routing

Check:

- correct route;

- elevation;

- coordination;

- no conflict with structure/other services;

- access maintained.

Pipe size

Compare installed diameter with approved drawings.

Joints

Inspect according to system type:

- threaded;

- soldered/brazed;

- grooved;

- welded;

- press-fit;

- flanged;

as applicable.

Look for:

- incomplete joints;

- misalignment;

- excessive strain;

- leakage evidence;

- improper fitting use.

Supports

Check:

- type;

- spacing;

- attachment;

- no unsupported long runs;

- support near valves/equipment where required;

- no improper support from other services.

Valves

Check:

- correct type;

- location;

- orientation;

- accessibility;

- tagging;

- operation.

Penetrations

Check:

- sleeve/opening;

- clearance;

- sealing;

- firestop where required;

- waterproofing/acoustic interface where applicable.

Testing

Where specified:

- pressure test;

- leak test;

- flushing;

- disinfection;

- test pressure;

- duration;

- gauge calibration/status;

- pass/fail.

Insulation

Inspect after successful testing unless project sequence states otherwise.

8.1.6 RECORDS / EVIDENCE

Capture:

- system/zone;

- pipe type/size;

- approved submittal reference;

- routing photos;

- supports;

- valve locations;

- penetrations;

- pressure-test record;

- flushing/disinfection record;

- insulation;

- deficiencies;

- corrective/retest evidence.

Traceability target:

Which section was tested, when, at what criterion, with what result, and what happened if it failed?

8.1.7 NC / DEFICIENCY

Typical:

- wrong pipe material;

- wrong diameter;

- unapproved fitting;

- poor joint;

- missing support;

- inaccessible valve;

- pipe routed through wrong opening;

- unsealed rated penetration;

- leak during test;

- insulation installed before test;

- wrong identification.

8.1.8 CORRECTIVE ACTION — EXAMPLE

Pressure test drops below acceptance criterion.

Identify test section → confirm test setup → locate leak → document → repair approved joint/component → repeat full required test → record passing result → only then proceed to insulation/concealment.

8.1.9 VERIFICATION

Confirm:

- repaired location;

- full retest passed;

- valve access;

- supports intact;

- penetrations resealed;

- insulation restored where disturbed.

8.1.10 CLOSURE

☐ approved material
☐ routing correct
☐ size correct
☐ joints accepted
☐ supports accepted
☐ valves complete/accessibly located
☐ penetrations complete
☐ testing passed
☐ flushing/disinfection complete where required
☐ insulation complete
☐ identification complete
☐ records filed

8.1.11 REPORTING / ANALYSIS

Track:

- recurring leaks;

- repeated support issues;

- inaccessible valves;

- frequent coordination clashes;

- repeated test failures;

- recurring penetration/firestop defects.

8.1.12 QUALITY CHECKPOINT

☐ Approved pipe/fittings
☐ Correct size
☐ Correct route
☐ Joints
☐ Supports
☐ Valves
☐ Access
☐ Penetrations
☐ Test complete
☐ Insulation
☐ Identification
☐ Closure evidence

8.2 SANITARY DRAINAGE

Quality objective

Install sanitary drainage with correct pipe material, routing, slope, joints, supports, cleanouts, vents and connections so wastewater drains reliably and remains accessible for maintenance.

8.2.1 REQUIREMENTS

Obtain:

- sanitary plans;

- riser diagrams;

- fixture schedules;

- pipe specifications;

- slope requirements;

- cleanout details;

- venting diagrams;

- support details;

- penetration/firestop details;

- test requirements;

- approved shop drawings;

- PIE/PRIE.

Extract:

- pipe size;

- material;

- slope;

- invert;

- cleanout locations;

- vent connections;

- test method;

- access requirements.

8.2.2 PLANNING

Before installation:

- coordinate gravity flow;

- verify elevations;

- identify slab/foundation penetrations;

- coordinate cleanouts;

- ensure access;

- identify test sections;

- plan pre-concealment inspection.

8.2.3 DOCUMENT CONTROL

Verify:

☐ latest sanitary plan
☐ current riser
☐ current slope/invert requirements
☐ current cleanout locations
☐ approved pipe material
☐ latest changes

8.2.4 MATERIAL CONTROL

Check:

- pipe;

- fittings;

- cleanouts;

- couplings;

- supports;

- access covers;

- sealants;

- firestop materials.

8.2.5 INSPECTION / TESTING

Check:

Routing

Correct branch/riser route.

Slope

This is critical.

Verify actual slope against project requirement.

Watch for:

- reverse slope;

- flat spots;

- sagging;

- localized low points.

Joints

Check:

- alignment;

- insertion/engagement;

- seals;

- clamps where applicable;

- no visible damage.

Supports

Check:

- adequate spacing;

- no sagging;

- pipe protected from movement.

Cleanouts

Verify:

- required locations;

- accessible;

- correct orientation;

- not concealed behind inaccessible finishes.

Venting

Verify routing and connection against approved drawings.

Testing

Where required:

- water test;

- air test;

- leak test;

- other specified test.

8.2.6 RECORDS / EVIDENCE

Capture:

- branch/riser;

- pipe material/size;

- slopes;

- cleanouts;

- concealed routing;

- test records;

- penetrations;

- corrections.

8.2.7 NC / DEFICIENCY

Common:

- wrong slope;

- reverse slope;

- inaccessible cleanout;

- unsupported pipe;

- leaking joint;

- wrong connection;

- pipe buried before test;

- unsealed penetration.

8.2.8 CORRECTIVE ACTION — EXAMPLE

Branch line has reverse slope over 2 m.

Measure → identify extent → hold concealment → reset supports/pipe → remeasure slope → repeat leak/test if required → photograph → close.

8.2.9 VERIFICATION

Confirm:

- slope corrected;

- no residual sagging;

- test passed;

- access preserved.

8.2.10 CLOSURE

☐ correct material
☐ size correct
☐ routing correct
☐ slope accepted
☐ joints accepted
☐ supports complete
☐ cleanouts accessible
☐ tests passed
☐ penetrations complete
☐ records complete

8.2.11 REPORTING / ANALYSIS

Track recurring:

- slope issues;

- cleanout access errors;

- leaks;

- support problems;

- premature concealment.

8.2.12 QUALITY CHECKPOINT

☐ Pipe material
☐ Size
☐ Route
☐ Slope
☐ Joints
☐ Supports
☐ Cleanouts
☐ Vents
☐ Test
☐ Penetrations
☐ Access
☐ Closure

8.3 STORM DRAINAGE

Quality objective

Install storm drainage with proper sizing, slope, support and connection so roof/site water is conveyed without leakage, ponding or uncontrolled discharge.

The workflow is similar to sanitary drainage but with strong interface to:

roof drains → vertical leaders → horizontal drainage → exterior system

8.3.1 REQUIREMENTS

Obtain:

- storm plans;

- roof drainage plan;

- plumbing risers;

- roof drain schedule;

- pipe specifications;

- slope requirements;

- overflow requirements;

- supports;

- insulation/condensation control;

- penetration details;

- test requirements;

- PIE/PRIE.

8.3.2 PLANNING

Coordinate:

- roof drains;

- leader locations;

- slab penetrations;

- exterior connections;

- overflow drainage;

- insulation;

- testing before concealment.

8.3.3 DOCUMENT CONTROL

Verify current:

☐ drain locations
☐ pipe sizes
☐ slopes
☐ overflow path
☐ connection point
☐ insulation requirement

8.3.4 MATERIAL CONTROL

Check:

- pipe;

- fittings;

- supports;

- insulation;

- drain bodies;

- cleanouts;

- couplings.

8.3.5 INSPECTION / TESTING

Inspect:

- roof drain connection;

- pipe routing;

- slope;

- supports;

- joints;

- cleanouts;

- penetrations;

- insulation;

- testing.

Check for potential condensation risk where specified insulation applies.

8.3.6 RECORDS

Capture:

- drain ID;

- leader route;

- test results;

- insulation;

- penetration;

- exterior connection.

8.3.7 NC / DEFICIENCY

Common:

- wrong drain connection;

- reverse/insufficient slope;

- leak;

- missing insulation;

- unsupported leader;

- wrong overflow connection.

8.3.8 CORRECTIVE ACTION

Correct route/slope/joint and retest.

8.3.9 VERIFICATION

Confirm drainage continuity and test result.

8.3.10 CLOSURE

☐ roof-drain connection
☐ route
☐ slope
☐ supports
☐ joints
☐ test
☐ insulation
☐ external connection
☐ records

8.3.11 REPORTING / ANALYSIS

Track repeated drainage leaks or coordination problems with roofing.

8.3.12 QUALITY CHECKPOINT

☐ Drain
☐ Pipe size
☐ Routing
☐ Slope
☐ Supports
☐ Joints
☐ Overflow
☐ Test
☐ Insulation
☐ Final connection

8.4 PROCESS / EQUIPMENT PIPING — WHERE APPLICABLE

This could be especially relevant on an electrical-substation project if mechanical support systems or equipment-related piping exist.

Quality objective

Install process/equipment piping exactly to approved system requirements, preserving material compatibility, routing, support, valve configuration, test integrity and equipment interfaces.

8.4.1 REQUIREMENTS

Obtain:

- process/mechanical schematics;

- P&IDs where applicable;

- equipment drawings;

- piping plans;

- isometrics;

- pipe specifications/classes;

- valve schedules;

- support details;

- approved shop drawings;

- test procedures;

- flushing/cleaning procedures;

- insulation requirements;

- commissioning requirements;

- PIE/PRIE.

8.4.2 PLANNING

Before work:

- identify system boundaries;

- isolate piping class;

- identify valves;

- identify equipment interfaces;

- define test packages;

- coordinate supports;

- identify inaccessible/critical joints.

8.4.3 DOCUMENT CONTROL

Verify:

☐ current P&ID/schematic
☐ current piping drawing/isometric
☐ approved material class
☐ valve schedule
☐ test procedure
☐ latest change

8.4.4 MATERIAL CONTROL

Check:

- pipe class/material;

- size;

- fittings;

- flanges;

- gaskets;

- bolts;

- valves;

- supports;

- identification;

- certifications where required.

For higher-spec systems, traceability can be especially important.

8.4.5 INSPECTION / TESTING

Check:

Routing

- correct route;

- slope if required;

- no unapproved low/high points;

- access.

Joints

Depending on system:

- welded;

- threaded;

- grooved;

- flanged;

- compression;

- other approved system.

Supports

Check:

- type;

- location;

- guide/anchor where specified;

- allowance for movement where applicable.

Valves

Check:

- type;

- orientation;

- flow direction;

- accessibility;

- tag.

Equipment interfaces

Verify:

- alignment;

- strain-free connection;

- flexible connectors where specified;

- service clearance.

Pressure/leak testing

Follow approved procedure.

Flushing/cleaning

Where required, verify documented completion.

8.4.6 RECORDS

Capture:

- system;

- line/segment;

- material;

- valve tags;

- test package;

- pressure test;

- flushing/cleaning;

- deficiencies;

- closure.

8.4.7 NC / DEFICIENCY

Common:

- wrong pipe class;

- wrong valve;

- reversed valve;

- poor joint;

- wrong support;

- failed pressure test;

- contamination;

- equipment connection under strain.

8.4.8 CORRECTIVE ACTION — EXAMPLE

Valve installed opposite required flow direction.

Identify valve/tag → verify drawing/flow arrow → control commissioning → reinstall correctly → retest affected section if required → update record → close.

8.4.9 VERIFICATION

Confirm:

- correct component;

- orientation;

- test;

- identification.

8.4.10 CLOSURE

☐ materials correct
☐ route correct
☐ joints accepted
☐ supports complete
☐ valves correct
☐ testing passed
☐ cleaning/flushing complete
☐ insulation/ID complete
☐ records complete

8.4.11 REPORTING / ANALYSIS

Track:

- recurring test failures;

- wrong valves/components;

- support conflicts;

- interface problems with equipment.

8.4.12 QUALITY CHECKPOINT

☐ Material/class
☐ Size
☐ Routing
☐ Joints
☐ Supports
☐ Valves
☐ Equipment interface
☐ Pressure test
☐ Flush/clean
☐ Insulation
☐ Identification

8.5 HVAC DUCTWORK

Quality objective

Install ductwork of the correct material, dimensions and routing, securely supported and sealed, with proper dampers, access and coordination, while maintaining required airflow pathways and system accessibility.

8.5.1 REQUIREMENTS

Obtain:

- HVAC plans;

- duct layouts;

- sections;

- equipment connections;

- duct schedules;

- approved shop drawings;

- ductwork specifications;

- pressure class;

- seal class;

- support details;

- insulation requirements;

- damper schedules;

- access-door requirements;

- fire/smoke damper details;

- testing requirements;

- PIE/PRIE.

Extract:

- duct size;

- material;

- gauge/construction;

- route;

- seal class;

- support spacing;

- insulation;

- damper type;

- access requirement.

8.5.2 PLANNING

Before installation:

- coordinate ceiling space;

- verify route;

- identify structural clashes;

- identify dampers;

- identify access doors;

- coordinate diffusers/grilles;

- identify insulation/test sequence;

- inspect concealed ductwork before ceilings close.

8.5.3 DOCUMENT CONTROL

Verify:

☐ current HVAC plan
☐ approved shop drawing
☐ duct size
☐ pressure/seal class
☐ damper schedule
☐ access requirements
☐ latest coordination changes

8.5.4 MATERIAL CONTROL

Check:

- duct material;

- gauge;

- fittings;

- sealants/tapes;

- flexible connectors;

- supports;

- dampers;

- access doors;

- insulation;

- labels.

8.5.5 INSPECTION / TESTING

Material

Correct duct construction.

Routing

Check:

- approved route;

- elevation;

- no clashes;

- no unauthorized field changes.

Dimensions

Verify duct size against drawing.

Joints

Check:

- connection;

- seal;

- mechanical fastening;

- no gaps.

Supports

Check:

- spacing;

- attachment;

- no excessive sag;

- independent support.

Sealing

Inspect:

- seams;

- joints;

- penetrations;

- sealant application.

Access

Ensure access to:

- dampers;

- coils;

- filters;

- controls;

- fire/smoke dampers.

Dampers

Check:

- correct type;

- location;

- orientation;

- access;

- actuator clearance where applicable.

Coordination

Check:

- lights;

- sprinkler;

- cable trays;

- ceilings;

- structure;

- equipment maintenance paths.

Testing

Where specified:

- leakage test;

- pressure test;

- airflow/balancing interface.

8.5.6 RECORDS / EVIDENCE

Capture:

- duct zone/system;

- size;

- support;

- damper;

- access doors;

- seal condition;

- test results;

- pre-concealment photos.

8.5.7 NC / DEFICIENCY

Common:

- wrong duct size;

- poor seal;

- missing support;

- inaccessible damper;

- wrong damper;

- unauthorized route change;

- dented/damaged duct;

- duct closed before inspection.

8.5.8 CORRECTIVE ACTION — EXAMPLE

Fire/smoke damper installed but no practical access is possible after ceiling closure.

Identify damper → verify access requirement → coordinate access panel → install/relocate panel or adjust layout → physically verify service access → document.

8.5.9 VERIFICATION

Confirm:

- duct route;

- seal;

- supports;

- damper/access;

- test pass.

8.5.10 CLOSURE

☐ duct material correct
☐ dimensions correct
☐ routing correct
☐ joints/seals accepted
☐ supports complete
☐ dampers correct/accessibly located
☐ insulation complete
☐ testing complete
☐ ceilings may close

8.5.11 REPORTING / ANALYSIS

Track:

- recurring leakage;

- inaccessible dampers;

- route clashes;

- poor support;

- repeated field modifications.

8.5.12 QUALITY CHECKPOINT

☐ Material
☐ Size
☐ Route
☐ Joints
☐ Supports
☐ Sealing
☐ Dampers
☐ Access
☐ Coordination
☐ Test
☐ Insulation
☐ Pre-concealment evidence

8.6 HVAC EQUIPMENT

Quality objective

Ensure approved HVAC equipment is received undamaged, installed in the correct location and orientation, securely supported, properly isolated, connected and accessible for operation and maintenance.

8.6.1 REQUIREMENTS

Obtain:

- equipment schedules;

- mechanical plans;

- approved equipment submittal;

- shop drawings;

- manufacturer installation instructions;

- equipment curb/base details;

- vibration-isolation requirements;

- service-clearance requirements;

- piping/duct/electrical connection details;

- commissioning/start-up requirements;

- PIE/PRIE.

8.6.2 PLANNING

Before delivery:

- verify final approved model;

- confirm base/curb ready;

- lifting/access plan;

- service clearances;

- duct/piping/electrical connections;

- drain requirements;

- vibration isolation;

- commissioning sequence.

8.6.3 DOCUMENT CONTROL

Verify:

☐ correct equipment tag
☐ approved model
☐ current shop drawing
☐ correct location/orientation
☐ current support/curb detail
☐ service clearances
☐ start-up requirements

8.6.4 MATERIAL CONTROL / RECEIVING

On receipt check:

- equipment tag/model;

- manufacturer;

- serial number;

- capacity/configuration;

- accessories;

- shipping damage;

- loose components;

- storage/protection;

- preservation requirements.

Take strong receiving photos for major equipment.

8.6.5 INSPECTION / TESTING

Location

Correct room/roof/location.

Orientation

Verify:

- service side;

- airflow direction;

- connection orientation.

Supports

Check:

- base;

- curb;

- anchors;

- structural support.

Clearances

Confirm:

- door removal;

- filter removal;

- coil access;

- motor access;

- control panel access;

- maintenance pathway.

Vibration isolation

Check:

- springs/pads;

- flexible connectors;

- isolation condition.

Connections

Verify:

- duct;

- pipe;

- drain;

- electrical;

- controls;

- grounding/bonding interfaces;

- flexible connections where specified.

Start-up/testing

Coordinate manufacturer/start-up record where required.

8.6.6 RECORDS / EVIDENCE

Capture:

- equipment tag;

- model/serial;

- receiving inspection;

- installation;

- anchors;

- vibration isolation;

- connections;

- clearances;

- start-up reports;

- deficiencies.

8.6.7 NC / DEFICIENCY

Common:

- wrong model;

- shipping damage;

- wrong orientation;

- inadequate maintenance clearance;

- missing isolation;

- misaligned connection;

- inadequate anchor;

- damaged curb/base;

- incomplete start-up.

8.6.8 CORRECTIVE ACTION — EXAMPLE

AHU installed so filter-access door cannot fully open.

Do not accept because “the unit fits.”

Confirm manufacturer service clearance → document conflict → coordinate relocation/adjacent-work modification → verify usable access → close.

Maintainability is a legitimate quality issue.

8.6.9 VERIFICATION

Confirm:

- equipment placement;

- support;

- clearance;

- connections;

- start-up;

- repairs.

8.6.10 CLOSURE

☐ correct equipment
☐ undamaged
☐ location/orientation correct
☐ supports/anchors accepted
☐ vibration isolation complete
☐ connections complete
☐ maintenance access adequate
☐ start-up/test complete
☐ documentation complete

8.6.11 REPORTING / ANALYSIS

Track:

- receiving damage;

- clearance problems;

- curb/base errors;

- repeated incomplete accessories;

- coordination failures.

8.6.12 QUALITY CHECKPOINT

☐ Tag/model
☐ Receiving condition
☐ Location
☐ Orientation
☐ Support/anchor
☐ Clearances
☐ Vibration isolation
☐ Duct connection
☐ Pipe connection
☐ Drain
☐ Electrical/control interface
☐ Start-up

8.7 MECHANICAL INSULATION

Quality objective

Provide continuous approved thermal/condensation-control insulation with correct thickness, vapour sealing, joint treatment and protection throughout mechanical systems.

8.7.1 REQUIREMENTS

Obtain:

- insulation specification;

- piping/duct schedule;

- approved products;

- thickness;

- vapour-barrier requirements;

- jacketing;

- outdoor/exposed protection;

- manufacturer instructions;

- PIE/PRIE.

8.7.2 PLANNING

Insulate only after:

- required pressure/leak testing passed;

- joints accepted;

- identification/test points documented;

- no unresolved leaks.

8.7.3 DOCUMENT CONTROL

Verify:

☐ system
☐ correct insulation type
☐ thickness
☐ vapour-control requirement
☐ jacketing
☐ latest changes

8.7.4 MATERIAL CONTROL

Check:

- insulation;

- thickness;

- facing;

- adhesive;

- vapour sealant;

- jacketing;

- fittings;

- condition/dryness.

8.7.5 INSPECTION

Check:

- continuous coverage;

- correct thickness;

- joints tight;

- valves/fittings treated appropriately;

- hangers/support interfaces;

- vapour barrier sealed;

- no compression;

- no wet insulation;

- outdoor/exposed protection.

For cold systems, vapour-control continuity is particularly important to prevent condensation.

8.7.6 RECORDS

Capture:

- system;

- thickness;

- fittings;

- vapour sealing;

- repairs;

- representative photos.

8.7.7 NC / DEFICIENCY

Common:

- wrong thickness;

- gaps;

- crushed insulation;

- open vapour seal;

- wet insulation;

- exposed joints;

- missing fitting insulation.

8.7.8 CORRECTIVE ACTION

Example:

Condensation-control insulation has open longitudinal vapour seam.

Open/prepare as required → reseal with approved system → verify continuity → photograph → close.

8.7.9 VERIFICATION

Confirm continuous insulation and vapour control.

8.7.10 CLOSURE

☐ type correct
☐ thickness correct
☐ continuous
☐ joints complete
☐ vapour seal complete
☐ fittings complete
☐ protection/jacketing complete

8.7.11 REPORTING / ANALYSIS

Track recurring gaps, damaged insulation or premature installation before testing.

8.7.12 QUALITY CHECKPOINT

☐ System tested first
☐ Correct product
☐ Thickness
☐ Continuity
☐ Joints
☐ Fittings
☐ Supports
☐ Vapour seal
☐ Jacketing
☐ No damage/moisture

8.8 MECHANICAL CONTROLS / BAS INTERFACES

Quality objective

Ensure physical controls devices and BAS interfaces are installed in the correct locations, connected to the intended equipment, accessible, identified and ready for functional commissioning.

You are not expected to program the BAS unless explicitly assigned.

8.8.1 REQUIREMENTS

Obtain:

- controls schematics;

- BAS points lists;

- mechanical control sequences;

- equipment shop drawings;

- controls shop drawings;

- sensor locations;

- damper/valve actuator details;

- control-panel layouts;

- commissioning requirements;

- PIE/PRIE.

8.8.2 PLANNING

Identify:

- equipment requiring controls;

- sensors;

- actuators;

- control panels;

- network/interface points;

- access requirements;

- commissioning sequence.

8.8.3 DOCUMENT CONTROL

Verify:

☐ current controls drawing
☐ current point list
☐ equipment tags
☐ sequence of operation
☐ current shop drawings

8.8.4 MATERIAL CONTROL

Check:

- sensors;

- actuators;

- thermostats;

- control panels;

- valves;

- dampers;

- cabling interfaces;

- labels.

8.8.5 INSPECTION / TESTING

Physical QC:

- correct device;

- correct location;

- accessibility;

- secure installation;

- correct equipment association;

- identification;

- sensor placement not obstructed;

- actuator linkage;

- control panel mounting;

- wiring interface complete.

Functional performance should be confirmed through commissioning/testing records.

8.8.6 RECORDS

Capture:

- device tag;

- equipment served;

- location;

- installation;

- functional-test/commissioning reference.

8.8.7 NC / DEFICIENCY

Common:

- sensor in wrong location;

- mislabeled device;

- inaccessible actuator;

- missing control device;

- wrong equipment association;

- incomplete commissioning.

8.8.8 CORRECTIVE ACTION

Correct installation/identification, then repeat required functional test.

8.8.9 VERIFICATION

Confirm physical correction and commissioning result.

8.8.10 CLOSURE

☐ devices installed
☐ tags correct
☐ access adequate
☐ equipment association correct
☐ functional test passed
☐ commissioning record complete

8.8.11 REPORTING / ANALYSIS

Track repeated controls coordination or commissioning failures.

8.8.12 QUALITY CHECKPOINT

☐ Device
☐ Location
☐ Tag
☐ Access
☐ Equipment interface
☐ Actuator/sensor
☐ Panel
☐ Commissioning result

8.9 MECHANICAL PENETRATIONS

This is a major multidisciplinary interface.

Quality objective

Ensure every mechanical penetration is correctly located and sized, structurally coordinated, properly sleeved/sealed and restored to the required fire, air, water, acoustic and finish performance.

8.9.1 REQUIREMENTS

Obtain:

- mechanical drawings;

- structural opening drawings;

- architectural details;

- firestop systems;

- waterproofing details;

- air-barrier details;

- roof details;

- sleeve details;

- approved coordination drawings;

- PIE/PRIE.

8.9.2 PLANNING

Before cutting/drilling:

- confirm location;

- verify structural approval;

- coordinate opening size;

- identify rated/waterproof/envelope condition;

- identify sleeve;

- identify final seal/firestop.

Rule

Never treat a penetration as only the mechanical trade's problem.

It belongs simultaneously to:

mechanical + structural + architectural/envelope + fire/life safety

8.9.3 DOCUMENT CONTROL

Verify:

☐ approved penetration
☐ current location
☐ opening size
☐ sleeve detail
☐ fire rating
☐ waterproof/air-barrier detail

8.9.4 MATERIAL CONTROL

Check:

- sleeve;

- firestop;

- sealant;

- boots;

- collars;

- waterproofing membrane;

- insulation;

- escutcheon/finish elements.

8.9.5 INSPECTION

Check:

- location;

- opening size;

- sleeve;

- clearance;

- no unauthorized structural damage;

- pipe/duct centered/configured correctly;

- firestop;

- air/water seal;

- insulation continuity;

- finish closure.

8.9.6 RECORDS

Capture:

- penetration ID/location;

- wall/floor type;

- service;

- firestop system;

- before/after photos;

- approval reference.

8.9.7 NC / DEFICIENCY

Common:

- unapproved core hole;

- oversize opening;

- cut reinforcement;

- missing sleeve;

- missing firestop;

- poor roof flashing;

- unsealed air-barrier interface;

- damaged insulation.

8.9.8 CORRECTIVE ACTION — EXAMPLE

Pipe penetrates rated wall but opening is larger than approved firestop system range.

Document dimensions → control closure → verify suitable listed firestop system or obtain authorized disposition → install approved solution → inspect → label/document → close.

8.9.9 VERIFICATION

Confirm:

- penetration system complete;

- structure unaffected/accepted;

- fire/water/air/acoustic continuity restored.

8.9.10 CLOSURE

☐ penetration approved
☐ location correct
☐ opening correct
☐ sleeve complete
☐ firestop/seal complete
☐ insulation restored
☐ architectural finish complete
☐ evidence filed

8.9.11 REPORTING / ANALYSIS

Track:

- unplanned penetrations;

- oversized openings;

- repeated late drilling;

- missing firestop;

- coordination failures.

8.9.12 QUALITY CHECKPOINT

☐ Approval
☐ Location
☐ Opening
☐ Sleeve
☐ Structure
☐ Firestop
☐ Waterproofing
☐ Air seal
☐ Insulation
☐ Finish
☐ Evidence

8.10 MECHANICAL TESTING

This section needs particularly strong traceability.

Quality objective

Demonstrate through approved testing, flushing, cleaning and balancing processes that mechanical systems are intact, clean, functional and ready for commissioning.

8.10.1 REQUIREMENTS

Obtain:

- testing specifications;

- PIE/PRIE;

- approved test procedures;

- system boundaries;

- test pressure/duration;

- leakage criterion;

- flushing requirements;

- cleaning requirements;

- balancing requirements;

- gauge/instrument calibration requirements;

- witness/hold requirements;

- commissioning plan.

8.10.2 PLANNING

Before test:

- identify test package;

- define system boundaries;

- ensure installation substantially complete;

- verify correct valves/caps/blinds;

- ensure gauges/instruments available;

- confirm calibration;

- notify required witnesses;

- ensure records/forms ready.

8.10.3 DOCUMENT CONTROL

Verify:

☐ approved procedure
☐ correct test package
☐ system drawing
☐ acceptance criterion
☐ current instrumentation requirement
☐ witness requirements

8.10.4 MATERIAL / EQUIPMENT CONTROL

Check:

- gauges;

- pumps;

- hoses;

- caps;

- blinds;

- temporary connections;

- flushing equipment;

- calibrated instruments;

- balancing instruments.

8.10.5 TESTING

Pressure tests

Verify:

- test medium;

- pressure;

- duration;

- starting condition;

- final reading;

- leak inspection;

- pass/fail.

Leak tests

Check:

- full test boundary;

- joint inspection;

- leakage criterion.

Flushing

Verify:

- correct section;

- flow path;

- required duration/velocity/condition where specified;

- discharge location;

- cleanliness evidence.

Cleaning

Confirm internal cleanliness requirements.

Balancing interface

You may not perform TAB yourself, but verify:

- system ready;

- dampers/valves accessible;

- approved TAB contractor where required;

- final report;

- unresolved deviations.

8.10.6 RECORDS / EVIDENCE

Every test package should identify:

- system;

- section;

- date/time;

- test procedure;

- criterion;

- instrument/gauge;

- calibration status;

- starting value;

- ending value;

- duration;

- witness;

- result;

- leaks/defects;

- repairs;

- retest;

- final acceptance.

8.10.7 NC / DEFICIENCY

Typical:

- failed pressure test;

- visible leak;

- gauge not calibrated;

- incomplete test boundary;

- test duration insufficient;

- flushing incomplete;

- dirty system;

- balancing report outside acceptance criteria.

8.10.8 CORRECTIVE ACTION — EXAMPLE

Domestic-water pressure test fails at one grooved joint.

Mark location → depressurize safely through responsible trade → repair joint → inspect → repeat complete required test → document passing retest → release for insulation.

8.10.9 VERIFICATION

Never close testing issue on repair alone.

Repair ≠ verification.

You need:

repair + required retest + passing evidence

8.10.10 CLOSURE

☐ test procedure followed
☐ criterion achieved
☐ gauges/instruments acceptable
☐ leaks resolved
☐ retesting passed
☐ flushing/cleaning complete
☐ balancing complete where required
☐ records signed/filed
☐ system ready for commissioning

8.10.11 REPORTING / ANALYSIS

Track:

- system test pass rate;

- recurrent leaking joint type;

- repeated gauge/calibration issues;

- repeated retesting;

- systems blocking commissioning.

8.10.12 QUALITY CHECKPOINT

☐ System identified
☐ Test boundary
☐ Procedure
☐ Criterion
☐ Instrument calibrated
☐ Witnesses
☐ Test performed
☐ Result documented
☐ Failure repaired
☐ Retest passed
☐ Record complete
☐ Commissioning-ready

8.11 MECHANICAL IDENTIFICATION

Identification may look minor, but it is essential for operations, maintenance, safety and commissioning.

Quality objective

Ensure mechanical equipment, pipes, valves and systems are clearly, consistently and durably identified according to project requirements.

8.11.1 REQUIREMENTS

Obtain:

- identification specification;

- equipment schedule;

- valve schedule;

- pipe identification requirements;

- colour coding;

- flow-arrow requirements;

- tag format;

- O&M requirements.

8.11.2 PLANNING

Before final identification:

- verify final equipment tags;

- confirm system names;

- coordinate with controls/BAS;

- ensure labels remain visible after insulation/ceiling work.

8.11.3 DOCUMENT CONTROL

Verify:

☐ equipment designation
☐ pipe system name
☐ valve tag
☐ colour/code
☐ flow direction

8.11.4 MATERIAL CONTROL

Check:

- labels;

- engraved tags;

- pipe markers;

- arrows;

- valve tags;

- adhesive/attachment system;

- durability.

8.11.5 INSPECTION

Equipment tags

Check:

- correct tag;

- readable;

- permanently attached;

- matches drawings/BAS.

Pipe identification

Check:

- system name;

- spacing/frequency;

- visible location;

- correct colour where required.

Flow arrows

Check:

- correct direction;

- visible;

- placed appropriately.

Valve identification

Check:

- tag present;

- matches valve schedule;

- accessible.

8.11.6 RECORDS

Capture:

- representative system labels;

- equipment tags;

- valve tags;

- discrepancies;

- final schedules.

8.11.7 NC / DEFICIENCY

Common:

- missing tag;

- wrong equipment ID;

- wrong flow arrow;

- label hidden behind ceiling;

- mismatched valve schedule;

- illegible identification.

8.11.8 CORRECTIVE ACTION

Replace/reposition/retag, then verify against current schedule.

8.11.9 VERIFICATION

Cross-check:

physical equipment → tag → drawing → schedule → BAS/O&M

where applicable.

8.11.10 CLOSURE

☐ equipment tagged
☐ piping identified
☐ valves tagged
☐ flow arrows correct
☐ labels visible
☐ schedules consistent

8.11.11 REPORTING / ANALYSIS

Track identification mismatches because they can reveal broader document-control discrepancies.

8.11.12 QUALITY CHECKPOINT

☐ Equipment tag
☐ Pipe label
☐ Flow arrow
☐ Valve tag
☐ Correct nomenclature
☐ Visibility
☐ Drawing/schedule match
☐ O&M consistency

MECHANICAL SERVICES — MASTER PRE-CONCEALMENT GATE

Before walls, shafts or ceilings close:

DOCUMENTATION

☐ Latest mechanical drawings
☐ Approved shop drawings
☐ Approved materials
☐ Technical changes incorporated

PIPING

☐ Correct material
☐ Correct size
☐ Routing
☐ Slopes
☐ Joints
☐ Supports
☐ Valves
☐ Access

DUCTWORK

☐ Correct material/size
☐ Routing
☐ Supports
☐ Sealing
☐ Dampers
☐ Access doors

PENETRATIONS

☐ Structural opening approved
☐ Sleeves
☐ Firestop
☐ Air/water seal
☐ Acoustic closure where applicable

TESTING

☐ Pressure/leak tests complete
☐ Failed tests corrected/retested
☐ Test records complete

INSULATION

☐ Only after required testing
☐ Correct type/thickness
☐ Vapour seal continuous

ACCESS

☐ Valves accessible
☐ Dampers accessible
☐ Equipment serviceable
☐ Controls accessible
☐ Access panels coordinated

EVIDENCE

☐ Photos
☐ Test records
☐ Inspection forms
☐ Deficiencies tracked
☐ Release obtained where required

MECHANICAL EQUIPMENT — COMMISSIONING READINESS GATE

Before calling equipment mechanically complete:

☐ Correct equipment received
☐ No unresolved shipping damage
☐ Correct location/orientation
☐ Anchors/supports complete
☐ Vibration isolation complete
☐ Duct connections complete
☐ Pipe connections complete
☐ Drainage complete
☐ Electrical interface complete
☐ Controls interface complete
☐ Filters/components installed
☐ Labels/tags complete
☐ Access/clearances maintained
☐ Start-up completed
☐ Functional testing available
☐ Deficiencies resolved

PRACTICAL EXAMPLE — PIPE ABOVE A FIRE-RATED CEILING

Suppose a mechanical contractor finishes piping above a ceiling and the architectural trade wants to close the ceiling tomorrow.

You do not merely inspect the pipe.

You cross-reference:

Mechanical → piping system
Mechanical → penetrations
Mechanical → testing
Mechanical → insulation
Interior Architectural → ceilings
Fire/Life Safety → firestopping

Your sequence becomes:

1. Requirements

Identify:

- approved piping;

- route;

- supports;

- test requirement;

- insulation;

- penetration fire rating;

- required access.

2. Physical installation

Check:

- pipe size/material;

- routing;

- supports;

- valves;

- slope if relevant.

3. Testing

Ask:

Has this concealed section actually passed the required pressure/leak test?

If not, ceiling closure should be questioned/controlled under the project procedure.

4. Penetrations

Check all rated-wall/floor crossings.

5. Insulation

Check after successful testing.

6. Access

Identify any valve requiring future access.

7. Evidence

Photograph the entire hidden system before ceiling closure.

Now, if there is ever a future dispute, you have evidence of what existed before concealment.

PRACTICAL EXAMPLE — HVAC UNIT ARRIVES ON SITE

An AHU arrives.

Your mental flow becomes:

Approved equipment?
→ Receiving damage?
→ Correct tag/model?
→ Correct base/curb?
→ Correct orientation?
→ Maintenance clearance?
→ Anchorage?
→ Vibration isolation?
→ Duct/piping/drain connections?
→ Electrical/controls interfaces?
→ Start-up?
→ Commissioning?

That is how the system prevents you from thinking:

“Equipment is sitting there, therefore installation is good.”

BUILD 2 — MECHANICAL SERVICES STATUS

8.1 Plumbing — Domestic Water ✓
8.2 Sanitary Drainage ✓
8.3 Storm Drainage ✓
8.4 Process/Equipment Piping ✓
8.5 HVAC Ductwork ✓
8.6 HVAC Equipment ✓
8.7 Mechanical Insulation ✓
8.8 Mechanical Controls/BAS Interfaces ✓
8.9 Mechanical Penetrations ✓
8.10 Mechanical Testing ✓
8.11 Mechanical Identification ✓

Yes. For Electrical Building Services, we need the same thoroughness as Mechanical, but with a firmer boundary around technical authority because Hochelaga is an electrical-substation project.

The governing principle should be explicit at the top of this module:

You are controlling building-quality execution, documentation, approved materials, physical installation, interfaces, traceability, testing evidence, and closure. You are not independently approving specialized electrical engineering criteria unless the PIE/PRIE and project authority specifically assign that responsibility to you.

Where the issue involves specialized electrical acceptance, protection, energization, cable testing, electrical safety, grounding-system performance, equipment internal configuration, or design interpretation:

🟠 VERIFY APPLICABLE PIE/PRIE → COORDINATE WITH RESPONSABLE QUALITÉ / AUTHORIZED ELECTRICAL SPECIALIST.

9. ELECTRICAL BUILDING SERVICES

The overall quality objective is:

Ensure building electrical systems are constructed from approved materials and equipment, installed in the correct locations and configuration, physically secure and accessible, coordinated with structural/architectural/mechanical systems, properly identified, tested by the appropriate qualified personnel, and fully documented before energization and turnover.

The universal electrical QC flow is:

Approved documents/materials → routing/layout → physical installation → supports → penetrations/interfaces → equipment installation → grounding/bonding interfaces → identification → testing evidence → deficiency correction → verification → closure

9.1 CONDUITS / RACEWAYS

Quality objective

Install the correct approved raceway system along the required route, with suitable supports, bends, fittings, penetrations, environmental protection and accessibility, without damaging adjacent systems or compromising future cable installation.

9.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- electrical plans;

- conduit/raceway layouts;

- electrical room layouts;

- riser diagrams;

- underground-electrical drawings;

- approved coordination drawings;

- conduit specifications;

- approved material submittals;

- support/hanger details;

- penetration details;

- firestop details;

- equipment/shop drawings;

- embedded-conduit drawings;

- Plan Qualité;

- applicable PIE/PRIE;

- approved procedures;

- technical directives;

- QMT/RFI responses.

Extract:

- raceway type;

- material;

- diameter;

- route;

- elevation;

- burial/encasement requirements where applicable;

- fittings;

- bend requirements;

- support spacing;

- expansion provisions;

- environmental/corrosion protection;

- penetration details;

- required testing/verification;

- identification requirements.

9.1.2 PLANNING

Before installation:

- identify system/route;

- check coordination with structure, ductwork, piping and cable trays;

- identify wall/slab penetrations;

- identify embedded conduits before concrete;

- identify hazardous/wet/exterior areas if applicable;

- coordinate access;

- identify areas becoming concealed;

- identify draw-box/pull-box locations;

- know whether installation must be inspected before cable pulling.

High-value planning question

Will this conduit still be inspectable once concrete, drywall or ceiling closure happens?

If not, schedule inspection and evidence capture beforehand.

9.1.3 DOCUMENT CONTROL

Verify:

☐ latest electrical drawing
☐ current conduit route
☐ current size/type
☐ current coordination drawing
☐ latest equipment locations
☐ current penetration details
☐ technical changes incorporated
☐ current PIE/PRIE

9.1.4 MATERIAL CONTROL

Check:

- conduit type;

- diameter;

- wall thickness/class;

- fittings;

- couplings;

- connectors;

- bushings;

- pull boxes;

- junction boxes;

- supports;

- corrosion-resistant components;

- seals;

- identification.

Observe for:

- crushed conduit;

- deformed fittings;

- cracked PVC;

- damaged coating;

- contaminated interiors;

- unidentified materials.

9.1.5 INSPECTION / TESTING

Routing

Check:

- correct route;

- no unauthorized relocation;

- adequate clearance;

- no conflict with structure/MEP;

- maintainable arrangement.

Size

Compare installed conduit size with approved drawing/schedule.

Bends

Check:

- smooth bends;

- no kinking;

- no flattening;

- excessive accumulated bends controlled according to project requirements;

- bend radius per approved requirements.

Joints / fittings

Check:

- complete connection;

- correct fittings;

- secure engagement;

- required sealing;

- proper connectors at boxes/equipment.

Supports

Check:

- support type;

- spacing;

- attachment;

- no inappropriate support from duct/pipe;

- vertical runs secured;

- movement provisions where required.

Embedded conduits

Before concrete:

- route;

- spacing;

- cover/interface;

- termination;

- secure fixing;

- no conflict with reinforcement;

- no excessive congestion.

Underground conduits

Where applicable:

- trench/bedding;

- spacing;

- depth;

- duct-bank geometry;

- concrete encasement if required;

- separators/spacers;

- end locations;

- drainage/grade if specified;

- marker/identification.

Pull boxes / junction boxes

Check:

- correct location;

- accessibility;

- dimensions/type;

- covers;

- support;

- identification.

Raceway continuity / readiness

Where required, verify appropriate specialist test or mandrel/pull-through evidence.

🟠 Specialized acceptance follows PIE/PRIE.

9.1.6 RECORDS / OBJECTIVE EVIDENCE

Capture:

- system/route;

- conduit size/type;

- concealed-route photos;

- embedded conduit photos;

- underground conduit photos;

- pull-box locations;

- support details;

- penetration details;

- inspection/test records;

- corrective/reinspection evidence.

For concealed conduit, strong evidence is especially valuable because later you may only see two ends emerging from concrete.

9.1.7 NC / DEFICIENCY

Common:

- wrong conduit type;

- wrong size;

- crushed conduit;

- excessive/unapproved route change;

- inadequate support;

- inaccessible pull box;

- conduit interfering with reinforcement;

- penetration not sealed;

- damaged corrosion protection;

- conduit covered before required inspection.

9.1.8 CORRECTIVE ACTION — EXAMPLE

Scenario

Conduit embedded in slab is found displaced from approved equipment stub-up location before pour.

Identify exact conduit/equipment → measure actual position → compare approved drawing → control pour locally → reposition and secure → remeasure → photograph → re-verify reinforcement/interface → close before concrete.

If discovered after concrete placement, do not improvise structural coring or offsets without authorized disposition.

9.1.9 VERIFICATION

Confirm:

- route corrected;

- size/material correct;

- supports complete;

- penetration restored;

- embedded conduit secure;

- test/readiness evidence complete.

9.1.10 CLOSURE

☐ correct raceway
☐ route correct
☐ size correct
☐ fittings complete
☐ supports complete
☐ penetrations complete
☐ boxes accessible
☐ concealed work documented
☐ required specialist verification complete
☐ records complete

9.1.11 REPORTING / ANALYSIS

Track:

- repeated route deviations;

- crushed conduits;

- missed stub-ups;

- support issues;

- unplanned coring;

- recurring MEP coordination problems.

9.1.12 QUALITY CHECKPOINT

☐ Drawing current
☐ Conduit type
☐ Size
☐ Route
☐ Bends
☐ Fittings
☐ Supports
☐ Boxes
☐ Penetrations
☐ Concealed-work evidence
☐ Required test/verification
☐ Closure

9.2 CABLE TRAYS

Quality objective

Install approved cable tray systems in the correct location, elevation and orientation, with complete supports, fittings, expansion provisions, bonding interfaces and usable clearances for cable installation and future maintenance.

9.2.1 REQUIREMENTS

Obtain:

- electrical plans;

- cable tray layouts;

- sections;

- coordination drawings;

- tray specifications;

- tray schedules;

- support details;

- manufacturer instructions;

- expansion details;

- bonding requirements;

- fire-rated penetration details;

- approved shop drawings;

- PIE/PRIE.

Extract:

- tray type;

- width/depth;

- route;

- elevation;

- loading/class;

- support spacing;

- bends/tees;

- expansion provisions;

- clearance;

- bonding;

- identification.

9.2.2 PLANNING

Before installation:

- review congested routes;

- coordinate with ductwork/piping/structure;

- identify vertical transitions;

- identify wall/fire separation penetrations;

- ensure future cable pulling space;

- maintain access above/below tray as required.

9.2.3 DOCUMENT CONTROL

Verify:

☐ latest tray routing
☐ correct tray size/type
☐ approved supports
☐ current coordination drawing
☐ current expansion details
☐ bonding detail current

9.2.4 MATERIAL CONTROL

Check:

- tray sections;

- fittings;

- bends;

- reducers;

- supports;

- splice plates;

- bonding jumpers where required;

- covers;

- fasteners;

- corrosion protection;

- damage.

9.2.5 INSPECTION / TESTING

Route

Check:

- correct path;

- elevation;

- no unapproved obstruction;

- adequate clearance.

Tray dimensions

Verify:

- width;

- depth;

- type.

Supports

Check:

- type;

- spacing;

- structural attachment;

- no sagging;

- vertical support.

Joints

Check:

- splice plates;

- fasteners;

- alignment;

- no sharp edges.

Expansion

Where required:

- expansion joints;

- movement allowance;

- bonding jumpers.

Penetrations

Verify:

- correct opening;

- firestop;

- edge protection;

- structural coordination.

Bonding

🟠 Verify physical bonding components against approved details; specialized electrical acceptance remains with authorized electrical personnel.

9.2.6 RECORDS / EVIDENCE

Capture:

- tray route;

- elevation;

- support installation;

- expansion joints;

- penetrations;

- bonding jumpers;

- deficiencies/corrections.

9.2.7 NC / DEFICIENCY

Typical:

- wrong tray size;

- poor alignment;

- inadequate supports;

- tray clashes;

- missing splice hardware;

- missing expansion provision;

- sharp/damaged edge;

- penetration not firestopped;

- insufficient access clearance.

9.2.8 CORRECTIVE ACTION — EXAMPLE

Tray installed below design elevation conflicts with mechanical piping.

Identify conflict → compare approved coordination drawings → control further installation → obtain coordinated resolution → adjust affected tray/piping as authorized → reinspect clearance/supports → document.

9.2.9 VERIFICATION

Confirm:

- correct route/elevation;

- supports;

- fittings;

- clearance;

- bonding interfaces;

- penetrations.

9.2.10 CLOSURE

☐ correct tray
☐ route/elevation accepted
☐ supports complete
☐ joints complete
☐ expansion addressed
☐ penetrations complete
☐ clearance maintained
☐ bonding interface complete
☐ ready for cable installation

9.2.11 REPORTING / ANALYSIS

Track recurring clashes, support failures or late routing changes.

9.2.12 QUALITY CHECKPOINT

☐ Tray type/size
☐ Route
☐ Elevation
☐ Alignment
☐ Supports
☐ Splices
☐ Expansion
☐ Clearance
☐ Penetrations
☐ Bonding interface
☐ Evidence

9.3 SUPPORTS / HANGERS

This should be a universal electrical support module.

Quality objective

Ensure electrical raceways, trays and equipment are supported independently and securely by approved systems connected to appropriate structure without unauthorized field modifications.

9.3.1 REQUIREMENTS

Obtain:

- support details;

- approved hanger systems;

- structural attachment details;

- seismic requirements where applicable;

- manufacturer instructions;

- spacing requirements;

- corrosion/environmental requirements;

- approved shop drawings;

- PIE/PRIE.

9.3.2 PLANNING

Before supports:

- identify structural attachment points;

- coordinate with post-tension/rebar where relevant;

- identify seismic bracing;

- coordinate crowded ceilings;

- avoid attachment to prohibited systems.

9.3.3 DOCUMENT CONTROL

Verify:

☐ support type
☐ spacing
☐ attachment method
☐ structural substrate
☐ seismic requirement
☐ current detail

9.3.4 MATERIAL CONTROL

Check:

- strut;

- rods;

- clamps;

- anchors;

- inserts;

- brackets;

- corrosion protection;

- seismic components.

9.3.5 INSPECTION

Check:

- support spacing;

- structural attachment;

- secure installation;

- vertical alignment;

- no excessive deflection;

- no support from unrelated services;

- anchor installation;

- seismic bracing where specified;

- corrosion protection.

🟠 Structural anchorage

If acceptance depends on anchor capacity, edge distance, embedment, pull testing, or engineered detail, verify through project requirement/authorized specialist.

9.3.6 RECORDS

Capture representative:

- supports;

- anchors;

- seismic bracing;

- deficiencies;

- corrective work.

9.3.7 NC / DEFICIENCY

Common:

- excessive spacing;

- missing support;

- improper attachment;

- support from duct/piping;

- unauthorized drilled anchor;

- damaged coating;

- missing seismic brace.

9.3.8 CORRECTIVE ACTION

Install/relocate approved support, repair affected substrate/coating, reinspect.

9.3.9 VERIFICATION

Confirm support stability and correct attachment.

9.3.10 CLOSURE

☐ approved support
☐ spacing correct
☐ attachment accepted
☐ bracing complete
☐ no unsupported sections
☐ records complete

9.3.11 REPORTING / ANALYSIS

Track recurring improper support practices across subcontractor crews.

9.3.12 QUALITY CHECKPOINT

☐ Support type
☐ Spacing
☐ Structural attachment
☐ Anchors
☐ Alignment
☐ Seismic bracing
☐ Corrosion protection
☐ No cross-trade support

9.4 ELECTRICAL EQUIPMENT INSTALLATION

Quality objective

Ensure approved electrical equipment is received undamaged and installed in the correct location/orientation with compliant anchorage, clearances, environmental protection, physical interfaces and full traceability.

This can include building-side:

- panels;

- transformers;

- disconnects;

- cabinets;

- motor-control equipment;

- distribution boards;

- control cabinets;

- UPS/battery-related building interfaces;

- other approved building electrical equipment.

🟠 Specialized substation process equipment may fall outside your building inspection authority.

9.4.1 REQUIREMENTS

Obtain:

- equipment schedules;

- electrical single-line drawings;

- equipment-room layouts;

- approved equipment submittals;

- shop drawings;

- manufacturer instructions;

- structural anchorage/base details;

- environmental requirements;

- clearance requirements;

- housekeeping pad details;

- grounding/bonding details;

- cable/conduit interfaces;

- test/start-up procedures;

- PIE/PRIE.

9.4.2 PLANNING

Before delivery:

- verify exact model/tag;

- verify room ready;

- housekeeping pad/base accepted;

- access path available;

- lifting path;

- service clearances;

- environmental conditions;

- conduit/cable interfaces;

- grounding/bonding interface;

- start-up/testing sequence.

9.4.3 DOCUMENT CONTROL

Verify:

☐ correct equipment tag
☐ approved manufacturer/model
☐ current shop drawing
☐ correct room/location
☐ anchorage detail
☐ clearance requirement
☐ environmental requirement
☐ latest revisions

9.4.4 MATERIAL CONTROL / RECEIVING

Inspect:

- manufacturer;

- model;

- tag;

- serial number;

- ratings/nameplate against approved submittal;

- accessories;

- shipping damage;

- moisture exposure;

- enclosure damage;

- missing components;

- storage/preservation.

Major equipment should have a strong receiving record.

9.4.5 INSPECTION / TESTING

Location

Correct room/grid/location.

Orientation

Correct service/access side.

Anchorage

Check:

- base;

- anchor bolts;

- quantity;

- physical installation;

- equipment level/plumb.

Clearances

Verify required:

- front working space;

- rear/side access where applicable;

- door opening;

- maintenance/removal access.

Do not invent electrical clearance values—use approved/code/project criteria.

Environmental protection

Check:

- indoor/outdoor enclosure;

- water exposure;

- dust;

- temporary protection;

- heating/ventilation requirements if specified.

Physical installation

Check:

- damage;

- doors/panels;

- covers;

- secure mounting;

- unused openings closed;

- penetrations complete;

- equipment housekeeping/pads complete.

Interfaces

Verify:

- conduit/cable entries;

- grounding connection;

- mechanical cooling/ventilation where applicable;

- controls;

- fire sealing.

🟠 Internal electrical terminations and specialized technical acceptance require authorized electrical inspection.

9.4.6 RECORDS / EVIDENCE

Capture:

- tag/model/serial;

- receiving inspection;

- nameplate;

- location;

- anchorage;

- clearances;

- equipment condition;

- penetrations;

- grounding interface;

- specialist test/start-up records.

9.4.7 NC / DEFICIENCY

Common:

- wrong model;

- shipping damage;

- insufficient clearance;

- wrong orientation;

- poor anchorage;

- damaged enclosure;

- unsealed openings;

- installation before room weather-tight;

- missing equipment identification.

9.4.8 CORRECTIVE ACTION — EXAMPLE

Panelboard installed where door cannot fully open because of adjacent mechanical equipment.

Document physical conflict → compare approved coordination/clearance requirement → prevent final acceptance → coordinate authorized relocation/modification → reinspect actual usable clearance → document closure.

9.4.9 VERIFICATION

Confirm:

- model/tag;

- location;

- anchor;

- clearances;

- environmental protection;

- specialist testing/status.

9.4.10 CLOSURE

☐ approved equipment
☐ receiving accepted
☐ correct location/orientation
☐ anchors complete
☐ clearances accepted
☐ environmental protection complete
☐ interfaces complete
☐ identification complete
☐ specialist testing accepted
☐ records complete

9.4.11 REPORTING / ANALYSIS

Track:

- shipping damage;

- clearance conflicts;

- late equipment changes;

- room-readiness issues;

- anchorage errors.

9.4.12 QUALITY CHECKPOINT

☐ Tag/model
☐ Nameplate
☐ Receiving condition
☐ Location
☐ Orientation
☐ Base/pad
☐ Anchorage
☐ Clearances
☐ Enclosure/protection
☐ Conduit/cable interface
☐ Grounding interface
☐ Identification
☐ Specialist test evidence

9.5 BUILDING DISTRIBUTION INTERFACES

This is intentionally an interface-control module, not a design module.

Quality objective

Ensure physical interfaces between building distribution equipment, feeders, panels, mechanical equipment, controls, emergency systems and architectural spaces are coordinated and complete.

9.5.1 REQUIREMENTS

Obtain:

- single-line diagrams;

- distribution plans;

- panel/equipment schedules;

- mechanical-equipment electrical requirements;

- controls drawings;

- emergency power drawings;

- equipment submittals;

- coordination drawings;

- PIE/PRIE.

9.5.2 PLANNING

Map interfaces:

- panel → equipment;

- transformer → panel;

- disconnect → mechanical unit;

- emergency source → emergency loads;

- control power;

- BAS interface;

- fire-alarm interfaces.

9.5.3 DOCUMENT CONTROL

Verify:

☐ equipment tags align
☐ feeders/interfaces current
☐ panel schedule current
☐ mechanical equipment requirements current
☐ latest technical changes

9.5.4 MATERIAL CONTROL

Check physical components where in scope:

- disconnects;

- boxes;

- equipment interfaces;

- raceways;

- identification;

- local control devices.

9.5.5 INSPECTION

Check physical coordination:

- correct equipment associated;

- local disconnect location/access;

- panel/equipment tags match;

- conduit entries complete;

- no obvious unsupported/unfinished interface;

- equipment clearances maintained;

- mechanical start-up dependencies understood.

🟠 Electrical rating, protection settings, feeder sizing and internal acceptance are specialized electrical matters.

9.5.6 RECORDS

Capture:

- interface/equipment tag;

- physical completion;

- labels;

- deficiencies;

- specialist acceptance reference.

9.5.7 NC / DEFICIENCY

Common:

- disconnect serving wrong equipment;

- inaccessible local disconnect;

- equipment/tag mismatch;

- missing raceway/interface;

- incomplete controls coordination.

9.5.8 CORRECTIVE ACTION

Coordinate correction, then verify physical and documentation alignment.

9.5.9 VERIFICATION

Cross-check:

drawing → equipment tag → physical installation → specialist test record

9.5.10 CLOSURE

☐ physical interface complete
☐ tags aligned
☐ access maintained
☐ specialist electrical acceptance available
☐ equipment ready for commissioning

9.5.11 REPORTING / ANALYSIS

Track recurring tag/interface or multidisciplinary coordination problems.

9.5.12 QUALITY CHECKPOINT

☐ Drawing
☐ Equipment tag
☐ Panel/disconnect interface
☐ Access
☐ Conduit/raceway
☐ Controls interface
☐ Emergency interface
☐ Specialist acceptance

9.6 GROUNDING / BONDING — WITHIN ASSIGNED INSPECTION SCOPE

Quality objective

Verify the physical installation, continuity intent, identification and documented specialist acceptance of grounding/bonding components within the assigned building scope.

This is where your boundary needs to be especially clear.

You can inspect:

- physical conductor presence;

- routing;

- mechanical connection;

- bonding jumpers;

- equipment grounding interfaces;

- visible corrosion/damage;

- labeling;

- test documentation.

You should not independently certify grounding-system performance unless formally authorized.

9.6.1 REQUIREMENTS

Obtain:

- grounding drawings;

- grounding details;

- bonding diagrams;

- equipment shop drawings;

- grounding conductor schedules;

- connection details;

- approved materials;

- testing requirements;

- PIE/PRIE.

9.6.2 PLANNING

Identify:

- concealed grounding components;

- structural steel interfaces;

- equipment connections;

- buried grounding;

- testing sequence;

- inspection before concealment.

9.6.3 DOCUMENT CONTROL

Verify:

☐ current grounding drawing
☐ conductor/type
☐ connection detail
☐ equipment bonding detail
☐ test requirements

9.6.4 MATERIAL CONTROL

Check:

- conductor;

- clamps/connectors;

- bonding jumpers;

- lugs;

- exothermic-weld materials where applicable;

- corrosion protection;

- identification.

9.6.5 INSPECTION / TESTING

Physical checks:

- conductor installed;

- correct route;

- connections complete;

- bonding jumpers present;

- equipment connection present;

- no visible damage;

- corrosion protection;

- concealed joints documented.

🟠 For continuity/resistance testing:

Verify test required by PIE/PRIE → witness/obtain results as assigned → authorized electrical specialist determines technical acceptance.

9.6.6 RECORDS

Capture:

- grounding point ID;

- conductor;

- connection type;

- photos before concealment;

- test report reference;

- corrections.

9.6.7 NC / DEFICIENCY

Common:

- missing bond;

- loose/incomplete visible connection;

- damaged conductor;

- unprotected connection;

- concealed before required inspection;

- missing test evidence.

9.6.8 CORRECTIVE ACTION

Correct physical installation according to approved detail, then repeat specialist test if affected.

9.6.9 VERIFICATION

Confirm:

- connection restored;

- protection complete;

- test result accepted by authorized specialist.

9.6.10 CLOSURE

☐ physical installation complete
☐ concealed work documented
☐ bonding complete
☐ test evidence available
☐ specialist acceptance recorded

9.6.11 REPORTING / ANALYSIS

Track recurring missed bonds, inaccessible connection points or missing test records.

9.6.12 QUALITY CHECKPOINT

☐ Drawing
☐ Conductor
☐ Routing
☐ Connection
☐ Bonding jumper
☐ Equipment interface
☐ Corrosion protection
☐ Pre-concealment evidence
☐ Specialist test result

9.7 LIGHTING

Quality objective

Install approved luminaires in the correct locations, securely supported, aligned with architectural layouts, physically undamaged and properly coordinated with ceilings and controls.

9.7.1 REQUIREMENTS

Obtain:

- lighting plans;

- reflected ceiling plans;

- luminaire schedule;

- approved submittals;

- mounting details;

- controls drawings;

- emergency-designation information;

- manufacturer instructions;

- PIE/PRIE.

9.7.2 PLANNING

Coordinate:

- ceiling grid;

- architectural alignment;

- sprinkler/diffuser/detector locations;

- supports;

- control zones;

- access.

9.7.3 DOCUMENT CONTROL

Verify:

☐ correct fixture type
☐ current layout
☐ mounting detail
☐ control zone
☐ latest changes

9.7.4 MATERIAL CONTROL

Check:

- fixture;

- model;

- finish;

- driver;

- lens;

- mounting hardware;

- damage.

9.7.5 INSPECTION / TESTING

Check:

- correct fixture;

- correct location;

- alignment;

- level/plumb;

- secure support;

- ceiling integration;

- no damage;

- controls interface;

- physical operation after specialist energization/testing.

🟠 Electrical circuit acceptance remains specialist scope.

9.7.6 RECORDS

Capture representative:

- fixture types;

- alignment;

- damage;

- functional test reference;

- deficiencies.

9.7.7 NC / DEFICIENCY

Common:

- wrong fixture;

- misalignment;

- damaged lens;

- unsupported fixture;

- fixture clashes with sprinkler/diffuser;

- wrong control zone.

9.7.8 CORRECTIVE ACTION

Reposition/replace/support correctly, then re-test function.

9.7.9 VERIFICATION

Confirm alignment and functional result.

9.7.10 CLOSURE

☐ correct fixture
☐ location correct
☐ support complete
☐ alignment accepted
☐ no damage
☐ controls/function verified
☐ records complete

9.7.11 REPORTING / ANALYSIS

Track repeated fixture/ceiling coordination issues.

9.7.12 QUALITY CHECKPOINT

☐ Fixture type
☐ Location
☐ Alignment
☐ Support
☐ Ceiling interface
☐ Condition
☐ Controls
☐ Functional evidence

9.8 EMERGENCY LIGHTING

Quality objective

Ensure emergency lighting and exit-related building systems are physically installed in the correct locations, identifiable and supported by required functional-test evidence.

9.8.1 REQUIREMENTS

Obtain:

- emergency lighting plans;

- life-safety plans;

- fixture schedule;

- exit-sign schedule;

- emergency-power interface;

- battery/unit-equipment requirements;

- testing/commissioning procedure;

- PIE/PRIE.

9.8.2 PLANNING

Identify:

- required fixtures;

- egress routes;

- exits;

- emergency circuits/power;

- functional test sequence.

9.8.3 DOCUMENT CONTROL

Verify:

☐ current emergency-light layout
☐ correct fixture type
☐ exit signs
☐ power/interface requirements
☐ test procedure

9.8.4 MATERIAL CONTROL

Check:

- emergency fixtures;

- battery units;

- exit signs;

- mounting hardware;

- labels;

- damage.

9.8.5 INSPECTION / TESTING

Physical checks:

- correct location;

- orientation;

- visibility;

- secure mounting;

- exit-sign direction;

- obstruction-free visibility.

Functional:

🟠 Verify required test is performed by authorized electrical personnel and obtain record.

9.8.6 RECORDS

Capture:

- fixture/exit ID;

- location;

- direction;

- functional-test record;

- deficiencies.

9.8.7 NC / DEFICIENCY

Common:

- missing fixture;

- exit sign pointing wrong direction;

- blocked visibility;

- failed battery/emergency test;

- damaged unit.

9.8.8 CORRECTIVE ACTION

Correct physical installation/component, repeat functional test.

9.8.9 VERIFICATION

Confirm visible, functional, correctly directed.

9.8.10 CLOSURE

☐ all required units installed
☐ locations/orientations correct
☐ exit signs correct
☐ functional testing passed
☐ records complete

9.8.11 REPORTING / ANALYSIS

Track failed emergency-system tests or repeated layout discrepancies.

9.8.12 QUALITY CHECKPOINT

☐ Location
☐ Fixture/sign type
☐ Orientation
☐ Visibility
☐ Mounting
☐ Emergency power
☐ Functional test
☐ Closure

9.9 ELECTRICAL PENETRATIONS

This is one of your most important building-quality electrical interfaces.

Quality objective

Ensure every electrical penetration is approved, properly located and sized, structurally coordinated, sealed, firestopped and integrated with air/water/acoustic control layers as applicable.

9.9.1 REQUIREMENTS

Obtain:

- electrical drawings;

- structural opening drawings;

- architectural details;

- fire-rated assembly drawings;

- firestop systems;

- air-barrier details;

- waterproofing/roof details;

- sleeve details;

- approved coordination drawings;

- PIE/PRIE.

9.9.2 PLANNING

Before coring/cutting:

- confirm approved location;

- determine wall/floor type;

- check structural implications;

- determine sleeve;

- identify rating;

- determine envelope/waterproofing implications.

Rule

No “we'll just drill here” approach.

9.9.3 DOCUMENT CONTROL

Verify:

☐ penetration approved
☐ location current
☐ opening size
☐ structural coordination
☐ firestop detail
☐ envelope detail

9.9.4 MATERIAL CONTROL

Check:

- sleeve;

- firestop;

- sealant;

- collars;

- putty/pads where applicable;

- boots;

- waterproofing materials;

- escutcheons.

9.9.5 INSPECTION

Check:

- location;

- opening dimensions;

- sleeve;

- no unauthorized structural damage;

- conduit/cable tray arrangement;

- firestop;

- air seal;

- waterproof seal;

- finish;

- labeling where required.

9.9.6 RECORDS

Capture:

- penetration ID/location;

- service;

- rated assembly;

- firestop system;

- before/after photos;

- approval.

9.9.7 NC / DEFICIENCY

Common:

- unauthorized core hole;

- oversize opening;

- cut reinforcing;

- missing firestop;

- incomplete roof flashing;

- unsealed conduit bundle;

- missing sleeve.

9.9.8 CORRECTIVE ACTION — EXAMPLE

Cable-tray penetration through rated wall exceeds limits of selected firestop system.

Identify opening/service dimensions → control closure → select/obtain authorized listed system → install approved solution → inspect → document → close.

9.9.9 VERIFICATION

Confirm structural/fire/envelope performance restored.

9.9.10 CLOSURE

☐ penetration approved
☐ structure accepted
☐ sleeve/opening accepted
☐ firestop complete
☐ air/water seal complete
☐ finish complete
☐ evidence filed

9.9.11 REPORTING / ANALYSIS

Track unplanned penetrations and repeat firestop deficiencies.

9.9.12 QUALITY CHECKPOINT

☐ Approval
☐ Location
☐ Opening size
☐ Structural interface
☐ Sleeve
☐ Firestop
☐ Air/water seal
☐ Finish
☐ Evidence

9.10 IDENTIFICATION / LABELS

Quality objective

Ensure electrical equipment, circuits, panels, raceways and relevant systems are clearly, correctly and permanently identified in accordance with project requirements.

9.10.1 REQUIREMENTS

Obtain:

- equipment naming convention;

- panel schedules;

- identification specification;

- label requirements;

- warning signage;

- equipment tags;

- cable/raceway identification requirements;

- commissioning/O&M requirements.

9.10.2 PLANNING

Before final labeling:

- confirm final equipment names;

- confirm panel schedules;

- confirm system numbers;

- coordinate naming with controls/BAS/O&M.

9.10.3 DOCUMENT CONTROL

Verify:

☐ correct equipment tag
☐ correct panel name
☐ current schedule
☐ approved label format
☐ correct nomenclature

9.10.4 MATERIAL CONTROL

Check:

- engraved labels;

- printed labels;

- warning signage;

- durable tags;

- cable/raceway markers;

- attachment method.

9.10.5 INSPECTION

Check:

- correct label;

- correct equipment;

- readable;

- permanent;

- visible;

- consistent with drawings/schedules;

- warning labels present where required.

Cross-check

Physical equipment → label → drawing → panel/schedule → O&M

9.10.6 RECORDS

Capture representative labels and discrepancies.

9.10.7 NC / DEFICIENCY

Common:

- wrong tag;

- missing label;

- inconsistent naming;

- unreadable label;

- temporary handwritten label left as final;

- physical equipment doesn't match schedule.

9.10.8 CORRECTIVE ACTION

Retag/update records as authorized, then cross-check again.

9.10.9 VERIFICATION

Confirm naming consistency throughout documents and field.

9.10.10 CLOSURE

☐ equipment labels complete
☐ panel labels complete
☐ warning signs complete
☐ schedules consistent
☐ O&M naming aligned

9.10.11 REPORTING / ANALYSIS

Repeated label mismatches may reveal deeper document-control problems.

9.10.12 QUALITY CHECKPOINT

☐ Correct asset
☐ Correct tag
☐ Readable
☐ Permanent
☐ Visible
☐ Drawing match
☐ Schedule match
☐ O&M match

9.11 ELECTRICAL TESTING INTERFACES

This section should probably be one of the most disciplined parts of your system because it prevents false autonomy.

Quality objective

Ensure required electrical tests are properly planned, witnessed/documented as assigned, failures are controlled and retested, and technical acceptance is provided by the appropriate authorized electrical specialist.

You are not trying to become the test engineer.

Your quality role is to ensure:

required test exists → correct system is tested → procedure is current → evidence is complete → failure is controlled → retest occurs → authorized acceptance is recorded.

9.11.1 REQUIREMENTS

🔵 Obtain:

- electrical testing specifications;

- PIE/PRIE;

- approved test procedures;

- commissioning plan;

- equipment manufacturer procedures;

- cable-testing requirements;

- grounding-test requirements;

- functional-test requirements;

- instrument calibration requirements;

- witness/hold-point requirements;

- acceptance authority.

Possible tests may include, depending on scope:

- continuity;

- insulation resistance;

- grounding/bonding tests;

- cable tests;

- equipment functional tests;

- lighting/emergency tests;

- protection/control testing;

- energization checks;

- specialized substation tests.

🟠 Never assume which tests apply. Use actual PIE/PRIE.

9.11.2 PLANNING

Before test:

- identify equipment/system;

- define test boundary;

- confirm construction complete enough;

- approved procedure available;

- calibrated instruments available;

- responsible electrical specialist identified;

- witness personnel notified;

- safety/energization requirements addressed;

- test form ready.

9.11.3 DOCUMENT CONTROL

Verify:

☐ current approved test procedure
☐ correct equipment/system ID
☐ latest drawings
☐ acceptance criterion available to authorized tester
☐ instrument calibration current
☐ witness requirements known

9.11.4 MATERIAL / EQUIPMENT CONTROL

Check documentation for:

- test instruments;

- calibration certificates;

- leads/accessories;

- manufacturer test equipment where applicable.

You aren't calibrating equipment yourself; you verify required evidence exists.

9.11.5 TEST INTERFACE

Your field-quality questions:

What exactly is being tested?

Does equipment tag match test form?

Is approved procedure being used?

Are required witnesses present?

Are instruments identified/calibrated as required?

Was test completed?

What is the documented result?

Who has technical authority to accept it?

If test fails

The workflow is:

FAIL → identify affected equipment/system → prevent premature acceptance/energization as project procedure requires → document → technical investigation/correction → repeat required test → authorized acceptance → closure

9.11.6 RECORDS / OBJECTIVE EVIDENCE

A strong test record should include:

- system/equipment tag;

- date/time;

- test procedure reference;

- technician/company;

- witness;

- instrument ID;

- calibration status;

- test result;

- acceptance status;

- defect/failure;

- corrective work;

- retest result;

- authorized sign-off.

9.11.7 NC / DEFICIENCY

Typical:

- required test missing;

- wrong equipment tagged;

- expired/missing calibration evidence;

- test procedure not approved/current;

- failed test not controlled;

- test repeated without documenting original failure;

- equipment energized before required acceptance.

9.11.8 CORRECTIVE ACTION — EXAMPLE

Specialist test on electrical equipment returns a failed result.

Your response should not be:

“I think the reading looks close enough.”

Your response:

Record equipment tag/test → mark status as failed/open according to project procedure → notify Responsable qualité/authorized electrical specialist → allow technical team to diagnose/correct → obtain documented retest → ensure authorized specialist accepts result → update quality status.

9.11.9 VERIFICATION

Your verification is primarily process and evidence verification:

☐ correct equipment retested
☐ approved procedure used
☐ test evidence complete
☐ passing result documented
☐ authorized specialist acceptance obtained
☐ related deficiency/NC closed

9.11.10 CLOSURE

Electrical test item is complete when:

☐ required test performed
☐ documentation complete
☐ failed tests resolved
☐ retest passed
☐ specialist acceptance recorded
☐ equipment/system status updated
☐ commissioning/energization dependency cleared

9.11.11 REPORTING / ANALYSIS

Track:

- open electrical tests;

- failed tests;

- aging failures;

- repeated failure types;

- missing test documents;

- calibration issues;

- systems blocking commissioning.

A useful management view might be:

| System/Equipment | Test Required | Test Status | Defect | Retest | Specialist Acceptance |
| --- | --- | --- | --- | --- | --- |
| EQ-01 | Required | Pass | — | — | ✓ |
| EQ-02 | Required | Fail | Open | Pending | — |
| EQ-03 | Required | Pass | Corrected | Pass | ✓ |

This lets you manage quality status without pretending to be the electrical engineer.

9.11.12 QUALITY CHECKPOINT

☐ Correct equipment/system
☐ Applicable PIE/PRIE
☐ Approved procedure
☐ Qualified specialist
☐ Required witnesses
☐ Calibrated instruments
☐ Test performed
☐ Result documented
☐ Failure controlled
☐ Corrective work completed
☐ Retest passed
☐ Authorized specialist acceptance
☐ Status/records updated

ELECTRICAL — MASTER PRE-CONCEALMENT GATE

Before walls, slabs or ceilings hide building electrical work:

DOCUMENTS

☐ Latest electrical drawings
☐ Approved shop drawings
☐ Technical changes incorporated
☐ Applicable PIE/PRIE

RACEWAYS

☐ Correct conduit
☐ Correct route
☐ Correct size
☐ Supports
☐ Boxes
☐ Embedded conduits documented

CABLE TRAYS

☐ Route/elevation
☐ Supports
☐ Expansion/interface
☐ Clearance

PENETRATIONS

☐ Approved opening
☐ Structural interface
☐ Firestop
☐ Air/water seal

GROUNDING/BONDING

☐ Physical components installed
☐ Concealed connections documented
☐ Required specialist inspection/test coordinated

EVIDENCE

☐ Photos
☐ Inspection records
☐ Test records
☐ Deficiencies controlled
☐ Required release obtained

Only then should concealment proceed.

ELECTRICAL EQUIPMENT — PRE-ENERGIZATION QUALITY GATE

This is another very useful field screen.

Before equipment is treated as ready:

PHYSICAL INSTALLATION

☐ Correct equipment
☐ No unresolved damage
☐ Correct location
☐ Correct orientation
☐ Anchored
☐ Clearances maintained
☐ Enclosure complete
☐ Openings closed

INTERFACES

☐ Raceways complete
☐ Cables/terminations complete per electrical team
☐ Grounding/bonding interface complete
☐ Controls interfaces complete
☐ Firestopping complete
☐ Identification complete

DOCUMENTATION

☐ Approved drawings
☐ Manufacturer documents
☐ Test procedure
☐ Inspection records
☐ Deficiencies/NC status clear

SPECIALIZED ACCEPTANCE

☐ Required electrical tests completed
☐ Failed tests corrected/retested
☐ Authorized electrical specialist accepts technical results
☐ Energization authorization handled through official project process

That last line matters enormously:

Your field playbook should never become an unofficial energization authorization system.

PRACTICAL EXAMPLE 1 — CONDUITS BEFORE CONCRETE POUR

Tomorrow, concrete slab is being poured and several electrical conduits are embedded.

Your sequence becomes:

Electrical → Conduits/Raceways
cross-reference
Superstructure → Cast-in-Place Concrete → Embeds → Pre-Pour Gate

Before pour

Verify:

- current electrical drawing;

- conduit sizes;

- locations;

- stub-ups;

- equipment interfaces;

- conduit securing;

- rebar clashes;

- penetrations;

- future pull-box/interface;

- photos.

If one equipment stub-up is wrong:

Don't allow the urgency of the concrete truck to transform a known error into permanent concrete.

Control → correct → reinspect → photograph → release.

That is exactly where your system earns its value.

PRACTICAL EXAMPLE 2 — PANEL INSTALLATION

Electrical panel arrives.

You open:

Electrical → Equipment Installation

Check:

Approved model?
→ shipping damage?
→ correct room?
→ correct orientation?
→ housekeeping pad/base?
→ anchorage?
→ required clearances?
→ raceway entries?
→ grounding interface?
→ labels?

Then when specialized electrical testing happens:

Electrical → Testing Interfaces

You don't attempt to judge specialized test values from memory.

You verify:

correct equipment → correct test → approved procedure → qualified person → result → authorized acceptance → traceable record.

That is controlled autonomy, which is exactly what you want.

PRACTICAL EXAMPLE 3 — CABLE TRAY THROUGH FIRE-RATED WALL

This crosses four modules:

Electrical → Cable Trays
Electrical → Penetrations
Interior Architectural → Fire-Rated Assemblies
Fire/Life Safety → Firestopping

Your field process becomes:

Tray approved/location correct?
→ opening approved?
→ wall rating known?
→ correct listed firestop system identified?
→ opening/service configuration within system limits?
→ installation inspected?
→ photo/documentation?

Now the penetration has been managed as a building system interface, not merely “the electrician installed a tray.”

ELECTRICAL BUILDING SERVICES — MASTER QUALITY GATE

Before considering a building electrical zone quality-complete:

RACEWAYS / TRAYS

☐ Correct materials
☐ Routes accepted
☐ Supports accepted
☐ Penetrations complete
☐ Concealed work documented

EQUIPMENT

☐ Approved equipment
☐ Receiving accepted
☐ Installation accepted
☐ Anchors/clearances complete
☐ Environmental protection complete

INTERFACES

☐ Building distribution interfaces complete
☐ Mechanical interfaces coordinated
☐ Controls interfaces coordinated
☐ Fire/life-safety interfaces complete

GROUNDING/BONDING

☐ Physical installation complete within assigned scope
☐ Required specialist testing/acceptance available

LIGHTING

☐ Fixtures complete
☐ Emergency lighting complete
☐ Functional tests documented

IDENTIFICATION

☐ Equipment labels
☐ Panel labels
☐ Raceways/systems as required
☐ Drawings/schedules aligned

TESTING

☐ Applicable PIE/PRIE tests complete
☐ Failures documented
☐ Corrective actions complete
☐ Retests passed
☐ Authorized electrical specialist acceptance documented

QUALITY RECORDS

☐ Inspection forms
☐ Photographs
☐ Material approvals
☐ Test reports
☐ NCR/deficiency closure
☐ Responsable qualité updated

The central principle for this whole module is:

You should become highly autonomous in controlling the quality process without pretending to possess technical authority that belongs to the electrical specialists.

That is actually stronger professionalism than trying to know everything yourself. Your value is knowing what must be controlled, what evidence must exist, what requires escalation, who owns the technical decision, and whether the entire loop has been properly closed.

Yes. Fire & Life-Safety Construction should be treated as a high-control section of the QMS. The consequences of poor work here are different from an ordinary finish deficiency: something can look perfectly acceptable while the required fire-resistance or smoke-control performance has been compromised behind the finished surface.

The governing principle for this module should therefore be:

No fire/life-safety element should become concealed until its required configuration has been inspected, deficiencies resolved, and objective evidence captured.

And, just as with electrical:

Your role is to verify construction against approved documents, listed/approved systems, PIE/PRIE requirements and project procedures—not to redesign fire-protection assemblies or independently approve deviations requiring professional/specialist judgment.

Where an installation deviates from an approved/listed fire-resistance system:

🟠 HOLD/CONTROL AFFECTED WORK → DOCUMENT → RESPONSABLE QUALITÉ → APPROPRIATE PROFESSIONAL/SPECIALIST → APPROVED DISPOSITION → VERIFY → CLOSE.

10. FIRE & LIFE-SAFETY CONSTRUCTION

Overall quality objective

Preserve the intended fire-resistance, smoke-control, compartmentation, egress and fire-protection performance of the building by ensuring every applicable assembly, penetration, closure and interface is constructed according to the approved requirements and remains traceable through completion.

The universal workflow is:

Identify rated condition → establish approved assembly/system → verify materials → inspect construction progressively → control penetrations/interfaces → inspect before concealment → document → identify deficiencies/NCs → correct → reinspect → obtain specialist testing/acceptance where required → close

10.1 FIRE-RATED WALLS

Quality objective

Ensure every required fire-rated wall is constructed as the approved assembly, continuously from its required boundary to boundary, without unauthorized substitutions, openings, penetrations or discontinuities that compromise the assembly.

10.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- architectural life-safety/fire-separation plans;

- wall-type schedules;

- architectural plans;

- sections/details;

- reflected ceiling plans where relevant;

- approved fire-rated assembly details;

- specifications;

- approved material submittals;

- manufacturer instructions;

- firestop details;

- door/frame schedules;

- MEP penetration drawings;

- structural interfaces;

- Plan Qualité;

- applicable PIE/PRIE;

- QMT/RFI responses;

- technical directives;

- approved changes.

Extract:

- wall ID/type;

- required fire-resistance rating;

- construction;

- stud/block type;

- board type;

- number of layers;

- board orientation where specified;

- fasteners;

- joint treatment;

- insulation;

- wall termination;

- head-of-wall condition;

- openings;

- doors;

- penetrations;

- firestop requirements.

Fundamental question

For every rated wall, you should be able to answer:

What exact approved assembly is this supposed to be?

Without that answer, visual inspection alone is insufficient.

10.1.2 PLANNING

Before construction:

- identify all rated walls on plan;

- classify by wall type/rating;

- identify MEP penetrations;

- identify rated doors;

- identify structural interfaces;

- identify head-of-wall condition;

- identify concealed layers;

- determine inspection stages;

- coordinate trades before closing walls.

Suggested inspection stages:

Framing → first-side board → services/penetrations → insulation/internal components → opposite-side board → joints/firestop → final condition

This prevents trying to inspect an entire assembly after everything has disappeared.

10.1.3 DOCUMENT CONTROL

Verify:

☐ latest life-safety plan
☐ current wall type
☐ required rating
☐ approved assembly
☐ current materials
☐ penetration details
☐ head-of-wall detail
☐ door/opening details
☐ latest technical changes

10.1.4 MATERIAL CONTROL

Check:

- studs/tracks or masonry;

- gypsum board type;

- board thickness;

- insulation;

- fasteners;

- joint compounds;

- sealants;

- firestop products;

- backing;

- head-of-wall products;

- approved labels/markings.

Look particularly for unauthorized substitution.

A board that looks like drywall does not establish that it is the specified fire-rated component.

10.1.5 INSPECTION / TESTING

Assembly identification

Confirm actual wall corresponds to approved wall type.

Framing

Check:

- stud type/gauge where specified;

- spacing;

- tracks;

- anchorage;

- openings;

- backing;

- head condition.

Boards

Check:

- approved board;

- thickness;

- required number of layers;

- orientation;

- joints;

- staggering where specified;

- fastener type/spacing;

- damaged board.

Insulation

Where part of assembly:

- approved type;

- thickness;

- continuity;

- no major gaps;

- properly positioned.

Continuity

Follow the wall physically.

Check:

- floor interface;

- structure above;

- corners;

- intersections;

- shafts;

- columns;

- curtain/envelope interfaces.

Penetrations

Every service penetration becomes a separate firestop control item.

Openings

Verify:

- door/frame;

- glazing where applicable;

- access panels;

- dampers;

- other openings;

are compatible with required assembly.

10.1.6 RECORDS / EVIDENCE

Capture:

- wall ID;

- location/grid/room;

- assembly reference;

- rating;

- framing;

- board markings;

- concealed layers;

- head-of-wall;

- penetrations;

- firestop;

- openings;

- representative fastener/joint condition;

- deficiencies;

- corrective work;

- final inspection.

Photographs should be taken before concealment, not merely after painting.

10.1.7 NC / DEFICIENCY

Typical:

- wrong board;

- missing layer;

- incorrect framing;

- excessive gaps;

- damaged board;

- incomplete wall above ceiling;

- improper head condition;

- unsealed penetration;

- unauthorized opening;

- incompatible access panel;

- incorrect rated-door interface.

10.1.8 CORRECTIVE ACTION — EXAMPLE

Rated wall requires two layers but a section has been closed with only one.

Identify affected wall/extent → control further finishing → document assembly requirement → remove/open as necessary → install missing approved layer → reinspect configuration → restore joints/finishes → document → close.

10.1.9 VERIFICATION

Confirm:

- approved assembly restored;

- concealed components verified;

- penetrations complete;

- interfaces complete;

- correction evidence retained.

10.1.10 CLOSURE

☐ correct wall type
☐ required rating confirmed
☐ materials approved
☐ framing accepted
☐ layers complete
☐ insulation complete where applicable
☐ head condition complete
☐ penetrations firestopped
☐ openings compliant
☐ pre-concealment evidence complete
☐ deficiencies closed

10.1.11 REPORTING / ANALYSIS

Track:

- rated walls inspected;

- walls awaiting concealment release;

- missing layers;

- penetration deficiencies;

- recurring subcontractor defects;

- reopened finished work.

Repeated deficiencies should trigger earlier inspection/intervention rather than simply producing more NCRs.

10.1.12 QUALITY CHECKPOINT

☐ Wall ID
☐ Rating
☐ Approved assembly
☐ Framing
☐ Board type
☐ Layers
☐ Fasteners/joints
☐ Insulation
☐ Head-of-wall
☐ Openings
☐ Penetrations
☐ Firestop
☐ Pre-concealment evidence
☐ Closure

10.2 FIRE-RATED FLOORS / CEILINGS

Quality objective

Ensure rated horizontal assemblies retain the complete approved configuration and are not compromised by openings, supports, recessed equipment or MEP penetrations.

10.2.1 REQUIREMENTS

Obtain:

- life-safety drawings;

- floor/ceiling assembly schedules;

- reflected ceiling plans;

- structural drawings;

- approved rated assemblies;

- ceiling details;

- MEP coordination drawings;

- penetration details;

- access-panel requirements;

- lighting/device details;

- firestop systems;

- PIE/PRIE.

Extract:

- required rating;

- assembly composition;

- board/layer requirements;

- suspension system;

- insulation;

- penetrations;

- permitted fixtures;

- access requirements.

10.2.2 PLANNING

Map:

- rated floors;

- rated ceilings;

- shafts;

- service penetrations;

- recessed fixtures;

- access panels;

- ducts;

- cable trays;

- pipes;

- structural penetrations.

Establish a pre-ceiling closure inspection.

10.2.3 DOCUMENT CONTROL

☐ latest life-safety drawing
☐ approved assembly
☐ current ceiling/floor details
☐ MEP coordination current
☐ penetration systems current

10.2.4 MATERIAL CONTROL

Check:

- gypsum/products;

- suspension components;

- insulation;

- fasteners;

- access panels;

- firestop;

- approved recessed devices.

10.2.5 INSPECTION

Check:

Assembly

- correct layers;

- correct materials;

- suspension/support;

- continuity.

Openings

- fixtures;

- diffusers;

- access panels;

- speakers/devices;

- ducts;

- pipes;

- conduits.

Interfaces

Check transitions to:

- walls;

- shafts;

- structure;

- exterior walls.

Penetrations

Verify firestop individually.

10.2.6 RECORDS

Capture:

- assembly/zone;

- rating;

- above-ceiling condition;

- MEP penetrations;

- firestop;

- access panels;

- deficiencies;

- closure evidence.

A panoramic pre-ceiling photo can be extremely useful in addition to detailed photos.

10.2.7 NC / DEFICIENCY

Typical:

- missing layer;

- unauthorized opening;

- incompatible access panel;

- unsealed penetration;

- incomplete perimeter;

- inappropriate recessed fixture;

- damaged rated assembly.

10.2.8 CORRECTIVE ACTION

Restore assembly according to approved detail/system.

10.2.9 VERIFICATION

Reinspect affected area before concealment.

10.2.10 CLOSURE

☐ assembly correct
☐ rating confirmed
☐ perimeter complete
☐ penetrations complete
☐ fixtures/openings accepted
☐ above-ceiling inspection complete
☐ evidence filed

10.2.11 REPORTING / ANALYSIS

Track closure readiness by room/zone.

10.2.12 QUALITY CHECKPOINT

☐ Assembly
☐ Rating
☐ Layers
☐ Supports
☐ Perimeter
☐ Openings
☐ MEP penetrations
☐ Access panels
☐ Firestop
☐ Evidence

10.3 FIRESTOPPING

This should be one of the most rigorous modules in the entire application.

The central concept is:

Firestop is not “red caulking around a pipe.” It is an approved system consisting of a specific assembly, opening, penetrating item, annular space, backing/fill material, firestop material, required depth/configuration and installation conditions.

10.3.1 REQUIREMENTS

Obtain:

- firestop specification;

- approved firestop submittals;

- listed/approved systems;

- penetration schedule;

- rated wall/floor details;

- manufacturer instructions;

- approved engineering judgments where applicable;

- PIE/PRIE;

- installer requirements;

- inspection requirements.

For every penetration determine:

- rated assembly;

- required rating;

- penetrating item;

- opening dimensions;

- penetrating-item dimensions;

- annular space;

- approved system;

- backing/fill;

- firestop product;

- required depth/thickness;

- installation sides;

- identification requirements.

10.3.2 PLANNING

Create a Firestop Penetration Register.

Suggested fields:

| ID | Location | Assembly | Rating | Service | Opening | Approved System | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FS-001 | Room X / Wall A | Rated wall | Req. | Pipe | Recorded | System Ref | Open |
| FS-002 | Electrical Room | Rated wall | Req. | Tray | Recorded | System Ref | Inspected |

Assign unique IDs where project procedures permit.

Coordinate inspection before shafts/walls/ceilings become inaccessible.

10.3.3 DOCUMENT CONTROL

For every system:

☐ approved/listed system reference
☐ current revision
☐ correct assembly
☐ correct penetrating item
☐ dimensional limits
☐ required products
☐ installation configuration

10.3.4 MATERIAL CONTROL

Check:

- manufacturer;

- product;

- batch/lot where project requires traceability;

- shelf life/expiry where applicable;

- storage;

- backing material;

- mineral wool/fill;

- collars;

- wraps;

- sealants;

- identification labels.

Do not accept product merely because the colour resembles other firestop.

10.3.5 INSPECTION / TESTING

For each penetration, inspect:

1. Assembly

Is it the wall/floor type covered by the system?

2. Penetrating item

- pipe?

- conduit?

- cable?

- cable bundle?

- tray?

- duct?

- insulated pipe?

Correct material and dimensions?

3. Opening size

Measure where required.

4. Annular space

Verify against approved system limits.

5. Backing

Check:

- type;

- density where specified;

- depth;

- placement.

6. Firestop material

Check exact approved product.

7. Depth / thickness

Verify required installed depth.

8. Configuration

- one side?

- both sides?

- collar?

- wrap?

- sealant?

- mineral wool?

- combination?

9. Finish

Check:

- continuity;

- voids;

- adhesion;

- complete perimeter.

10. Identification

Label where required.

10.3.6 PHOTOGRAPHIC TRACEABILITY

This deserves its own subsection.

For critical penetrations, capture:

Photo 1 — location/context

Shows where penetration is.

Photo 2 — opening/penetrating item

Before firestop where useful.

Photo 3 — backing/configuration

Before it becomes hidden.

Photo 4 — completed firestop

Shows final installation.

Photo 5 — identification label

Where applicable.

Photo naming can follow:

FS-### – Building/Room – Wall/Floor – Date – Stage

This turns random photos into objective quality records.

10.3.7 RECORDS / EVIDENCE

Retain:

- penetration ID;

- location;

- rated assembly;

- penetrating item;

- approved system;

- dimensions where required;

- product;

- inspection;

- photographs;

- deficiency;

- repair;

- reinspection;

- closure.

10.3.8 NC / DEFICIENCY

Common:

- wrong product;

- no approved system;

- excessive annular space;

- wrong backing;

- insufficient sealant depth;

- missing collar/wrap;

- incomplete perimeter;

- wrong penetrating-item configuration;

- damaged firestop;

- additional cables added after completed firestop;

- penetration concealed before inspection.

That last-but-one is important: a previously accepted firestop can become noncompliant after another trade modifies it.

10.3.9 CORRECTIVE ACTION — EXAMPLE

Scenario

Electrical contractor adds cables through an already completed penetration.

Workflow:

Identify FS ID → reopen quality status → compare modified configuration against approved system → remove/repair firestop as required → reinstall approved configuration → reinspect → photograph → update register → re-close.

Never assume the original acceptance remains valid.

10.3.10 VERIFICATION

Confirm:

- actual configuration matches approved system;

- repair complete;

- no voids;

- dimensions acceptable;

- label updated;

- photos complete.

10.3.11 CLOSURE

☐ penetration ID
☐ assembly identified
☐ rating identified
☐ approved system confirmed
☐ penetrating item correct
☐ opening acceptable
☐ annular space acceptable
☐ backing correct
☐ product correct
☐ depth/thickness correct
☐ configuration correct
☐ identification complete
☐ photographs complete
☐ deficiencies closed

10.3.12 REPORTING / ANALYSIS

Track:

- total penetrations;

- inspected;

- accepted;

- rejected;

- awaiting repair;

- awaiting specialist disposition;

- modified after acceptance;

- recurring defect types;

- recurring trade responsible.

This could become a genuinely useful Firestop Dashboard.

10.3.13 QUALITY CHECKPOINT

☐ System reference
☐ Assembly
☐ Rating
☐ Penetrating item
☐ Opening
☐ Annular space
☐ Backing
☐ Product
☐ Depth
☐ Configuration
☐ Finish
☐ Label
☐ Photos
☐ Reinspection
☐ Closure

10.4 FIRE / SMOKE DAMPERS

Quality objective

Ensure required fire/smoke dampers are the approved type, correctly located and oriented, installed with required interfaces and access, and supported by appropriate functional inspection/testing evidence.

10.4.1 REQUIREMENTS

Obtain:

- mechanical plans;

- life-safety plans;

- damper schedule;

- approved submittals;

- manufacturer instructions;

- rated assembly details;

- sleeve/retaining details;

- access requirements;

- controls/fire-alarm interface;

- testing requirements;

- PIE/PRIE.

10.4.2 PLANNING

Identify every required damper and map:

Damper ID → wall/floor → rating → duct → access → controls interface → test requirement

Inspect before ceilings close.

10.4.3 DOCUMENT CONTROL

☐ correct damper type
☐ location
☐ approved model
☐ rated assembly
☐ installation detail
☐ access requirement
☐ testing requirement

10.4.4 MATERIAL CONTROL

Check:

- damper;

- sleeve;

- retaining components;

- actuator;

- access door;

- labels;

- accessories.

10.4.5 INSPECTION / TESTING

Check:

- correct damper;

- location;

- orientation;

- sleeve;

- attachment;

- clearances;

- breakaway/duct interface where specified;

- wall/floor opening;

- firestop/interface;

- actuator;

- access.

Critical field question

Can someone actually reach, inspect, reset and maintain this damper after the building is finished?

Functional operation/testing:

🟠 Verify applicable PIE/PRIE → coordinate qualified mechanical/electrical/fire-alarm specialist as required → retain test evidence.

10.4.6 RECORDS

Capture:

- damper ID;

- location;

- model;

- wall/floor;

- installation;

- access;

- actuator;

- test result;

- deficiency/correction.

10.4.7 NC / DEFICIENCY

Common:

- wrong damper;

- wrong orientation;

- missing access;

- blocked blade;

- incorrect sleeve/interface;

- inaccessible actuator;

- incomplete firestop;

- failed functional test.

10.4.8 CORRECTIVE ACTION — EXAMPLE

Damper is correctly installed but inaccessible after ceiling closure.

Identify damper → verify access requirement → coordinate access panel/location → install → physically verify usable access → update documentation → close.

10.4.9 VERIFICATION

Confirm installation + access + functional acceptance.

10.4.10 CLOSURE

☐ correct damper
☐ location/orientation
☐ sleeve/interface
☐ access
☐ actuator
☐ firestop
☐ functional test
☐ specialist acceptance where required
☐ records complete

10.4.11 REPORTING / ANALYSIS

Track inaccessible dampers, installation deficiencies and test failures.

10.4.12 QUALITY CHECKPOINT

☐ ID
☐ Type
☐ Location
☐ Orientation
☐ Sleeve
☐ Attachment
☐ Rated interface
☐ Access
☐ Actuator
☐ Functional test
☐ Evidence

10.5 FIRE-RATED DOORS

Quality objective

Ensure rated door assemblies—including door, frame, glazing, hardware and surrounding wall interface—are installed as complete compatible assemblies and operate correctly.

10.5.1 REQUIREMENTS

Obtain:

- door schedule;

- life-safety plan;

- hardware schedule;

- approved door/frame submittals;

- rated assembly requirements;

- glazing requirements;

- manufacturer instructions;

- wall details;

- firestop/seal details;

- PIE/PRIE.

Extract:

- door ID;

- rating;

- door type;

- frame;

- hardware set;

- closer;

- latch;

- seals;

- glazing;

- threshold;

- hold-open/interface where applicable.

10.5.2 PLANNING

Track each rated door by ID.

Coordinate:

- wall construction;

- frame installation;

- hardware;

- electrical/fire-alarm interface;

- final operation inspection.

10.5.3 DOCUMENT CONTROL

☐ door schedule current
☐ rating
☐ frame
☐ hardware set
☐ glazing
☐ latest changes

10.5.4 MATERIAL CONTROL

Check:

- door label;

- frame label;

- hardware;

- closer;

- latch;

- hinges;

- seals;

- glazing;

- fasteners.

Do not paint over/remove required labels.

10.5.5 INSPECTION / TESTING

Check:

Door/frame

- correct ID;

- labels;

- frame anchorage;

- plumb/level;

- physical damage.

Clearances

Verify against approved requirements.

Hardware

Check:

- hinges;

- closer;

- latch;

- lock;

- panic hardware where required;

- seals.

Operation

Door should:

open → close → self-close where required → latch correctly

Glazing

Verify approved rated glazing where applicable.

Interfaces

Check:

- wall/frame perimeter;

- firestop/seal;

- hold-open device;

- fire-alarm release where applicable.

🟠 Specialized functional interface tests should follow PIE/PRIE.

10.5.6 RECORDS

Capture:

- door ID;

- labels;

- frame;

- hardware;

- final condition;

- functional test;

- deficiencies.

10.5.7 NC / DEFICIENCY

Typical:

- missing/damaged label;

- wrong hardware;

- door fails to latch;

- closer incorrectly adjusted;

- excessive gap;

- incompatible glazing;

- incomplete frame perimeter;

- blocked door.

10.5.8 CORRECTIVE ACTION — EXAMPLE

Rated door closes but does not latch.

Identify door → inspect alignment/hardware → adjust/repair using approved components → repeat full closing/latching test → document → close.

10.5.9 VERIFICATION

Don't simply inspect the repair.

Operate the door again.

10.5.10 CLOSURE

☐ door/frame correct
☐ labels intact
☐ rating confirmed
☐ hardware complete
☐ seals complete
☐ glazing accepted
☐ self-closing/latching works
☐ interfaces complete
☐ records complete

10.5.11 REPORTING / ANALYSIS

Track failed final door tests and recurring hardware deficiencies.

10.5.12 QUALITY CHECKPOINT

☐ Door ID
☐ Rating
☐ Door label
☐ Frame label
☐ Anchorage
☐ Clearances
☐ Hardware
☐ Seals
☐ Glazing
☐ Closing
☐ Latching
☐ Interface
☐ Closure

10.6 FIRE-ALARM PHYSICAL INSTALLATION INTERFACES

Here we maintain the same boundary used for electrical.

Quality objective

Verify the physical installation, location, identification, accessibility and building interfaces of fire-alarm components while leaving specialized system programming, circuit performance and acceptance testing to authorized personnel.

10.6.1 REQUIREMENTS

Obtain:

- fire-alarm plans;

- device layouts;

- riser diagrams;

- approved shop drawings;

- device schedule;

- manufacturer information;

- architectural reflected ceiling plans;

- mechanical interfaces;

- electrical interfaces;

- testing/commissioning requirements;

- PIE/PRIE.

10.6.2 PLANNING

Identify:

- control panels;

- detectors;

- pull stations;

- notification devices;

- supervisory devices;

- mechanical interfaces;

- damper interfaces;

- emergency systems;

- final integrated testing.

10.6.3 DOCUMENT CONTROL

☐ current fire-alarm drawing
☐ approved devices
☐ device IDs
☐ interface drawings
☐ testing requirements

10.6.4 MATERIAL CONTROL

Check physical:

- device type;

- model;

- labels;

- bases;

- cabinets;

- mounting accessories;

- damage.

10.6.5 INSPECTION / TESTING

You can inspect:

- correct physical device;

- approximate/location conformity against approved documents;

- mounting;

- accessibility;

- visibility;

- identification;

- obstruction;

- coordination with ceilings;

- physical interface completion.

For technical acceptance:

🟠 Verify applicable PIE/PRIE → authorized fire-alarm/electrical specialist performs required testing → obtain documented result.

Do not independently approve:

- programming;

- signal timing;

- circuit performance;

- cause/effect logic;

- specialized electrical values.

10.6.6 RECORDS

Capture:

- device ID;

- location;

- physical condition;

- installation;

- specialist test reference;

- deficiency.

10.6.7 NC / DEFICIENCY

Common:

- missing device;

- wrong device;

- obstructed device;

- incorrect physical location;

- damaged device;

- missing identification;

- incomplete specialist test.

10.6.8 CORRECTIVE ACTION

Correct physical installation → specialist retest where affected → document.

10.6.9 VERIFICATION

Confirm physical correction and required functional acceptance.

10.6.10 CLOSURE

☐ physical devices complete
☐ identification complete
☐ interfaces complete
☐ specialist tests passed
☐ deficiencies closed
☐ records filed

10.6.11 REPORTING / ANALYSIS

Track physical installation deficiencies separately from functional/commissioning failures.

10.6.12 QUALITY CHECKPOINT

☐ Device
☐ Location
☐ Mounting
☐ Accessibility
☐ Identification
☐ Interfaces
☐ Specialist testing
☐ Closure

10.7 EMERGENCY / LIFE-SAFETY INTERFACES

This module connects several systems rather than representing one trade.

Quality objective

Ensure the physical interfaces among emergency lighting, exit signage, fire alarm, doors, mechanical systems, emergency power and egress construction are complete and coordinated before final acceptance.

10.7.1 REQUIREMENTS

Obtain:

- life-safety plans;

- egress plans;

- emergency lighting plans;

- fire-alarm drawings;

- door/hardware schedules;

- mechanical controls;

- emergency-power documents;

- commissioning/integrated testing requirements;

- PIE/PRIE.

10.7.2 PLANNING

Build an interface matrix:

| Event/System | Related Interface |
| --- | --- |
| Fire alarm | Dampers |
| Fire alarm | Door releases |
| Emergency power | Emergency lighting |
| Egress | Exit signage |
| Rated separation | Doors/penetrations |
| Fire protection | Alarm/supervision |

The actual project documents determine which interfaces exist.

10.7.3 DOCUMENT CONTROL

Verify current documents across all affected disciplines, not only architectural/fire drawings.

10.7.4 MATERIAL CONTROL

Verify installed interface devices/components against approved submittals where assigned.

10.7.5 INSPECTION / TESTING

Physical QC:

- egress routes unobstructed;

- exit signs correctly located/oriented;

- emergency lighting installed;

- rated doors complete;

- interface devices physically installed;

- access maintained.

Integrated functional testing:

🟠 Coordinate with authorized specialists according to PIE/PRIE and commissioning requirements.

10.7.6 RECORDS

Capture:

- interface;

- systems involved;

- test reference;

- participants;

- result;

- deficiency;

- corrective action;

- retest.

10.7.7 NC / DEFICIENCY

Examples:

- door release doesn't operate during integrated test;

- exit sign orientation wrong;

- emergency light fails;

- damper fails commanded operation;

- interface not connected;

- egress route obstructed.

10.7.8 CORRECTIVE ACTION

Determine responsible discipline → correct → repeat affected integrated test.

10.7.9 VERIFICATION

This is important:

When an interface fails, testing only the repaired component may not be enough. The affected interface/function may need to be retested end-to-end according to the project requirements.

10.7.10 CLOSURE

☐ individual systems complete
☐ interfaces complete
☐ integrated tests passed where required
☐ failures corrected
☐ retests passed
☐ specialist acceptance documented

10.7.11 REPORTING / ANALYSIS

Track interface failures separately because they often reveal coordination problems rather than workmanship problems.

10.7.12 QUALITY CHECKPOINT

☐ Systems identified
☐ Interface defined
☐ Physical completion
☐ Specialist participation
☐ Functional test
☐ Failure correction
☐ Retest
☐ Acceptance

10.8 FIRE PROTECTION SYSTEMS — IF APPLICABLE

We'll structure this around building fire-protection piping/sprinkler-type systems without assuming Hochelaga's exact system.

Quality objective

Ensure fire-protection system components are approved, correctly installed, adequately supported and accessible, coordinated with building construction, and supported by required specialist testing and acceptance.

10.8.1 REQUIREMENTS

Obtain:

- fire-protection drawings;

- approved shop drawings;

- hydraulic/design documentation where applicable;

- specifications;

- pipe/fitting approvals;

- sprinkler/device schedules;

- support details;

- seismic details where applicable;

- valve requirements;

- penetration/firestop details;

- testing procedures;

- flushing requirements;

- commissioning requirements;

- PIE/PRIE.

🟠 Hydraulic design and specialist fire-protection engineering acceptance are outside your independent authority.

10.8.2 PLANNING

Before installation:

- review routing;

- coordinate ceilings;

- identify sprinkler/device locations;

- identify valves;

- identify test/drain connections;

- coordinate supports;

- identify penetrations;

- define testing sequence.

10.8.3 DOCUMENT CONTROL

☐ approved shop drawing
☐ pipe/material current
☐ head/device schedule
☐ supports current
☐ latest coordination drawing
☐ test procedure
☐ PIE/PRIE

10.8.4 MATERIAL CONTROL

Check:

- pipe;

- fittings;

- valves;

- heads/devices;

- supports;

- seismic components;

- identification;

- approved models;

- physical damage.

For sprinkler heads especially:

- correct approved type;

- finish;

- condition;

- protection until appropriate stage.

10.8.5 INSPECTION / TESTING

Piping

Check:

- approved material;

- size against approved documents;

- routing;

- joints;

- physical condition;

- accessibility.

Supports

Check:

- type;

- spacing;

- attachment;

- seismic bracing where applicable.

🟠 Engineered support/seismic acceptance follows approved design and specialist requirements.

Heads/devices

Check:

- correct type;

- location;

- orientation;

- physical damage;

- obstruction/coordination;

- ceiling interface.

Do not independently determine specialized coverage/design adequacy beyond approved drawings.

Valves

Check:

- correct location;

- accessibility;

- identification;

- physical installation.

Penetrations

Check firestop/rated assembly interface.

Testing

Potential requirements may include:

- pressure testing;

- flushing;

- alarm/interface testing;

- valve testing;

- integrated system testing.

🟠 Actual required tests and acceptance criteria come from project documents/PIE/PRIE and authorized fire-protection personnel.

10.8.6 RECORDS / EVIDENCE

Capture:

- system/zone;

- approved drawing;

- piping;

- supports;

- heads/devices;

- valves;

- penetrations;

- test report;

- deficiencies;

- repairs;

- retests;

- specialist acceptance.

10.8.7 NC / DEFICIENCY

Typical:

- wrong component;

- damaged head;

- missing support;

- inaccessible valve;

- piping clash;

- head obstructed by later construction;

- penetration not firestopped;

- failed pressure test;

- missing specialist test documentation.

10.8.8 CORRECTIVE ACTION — EXAMPLE

Sprinkler head location becomes obstructed after a large duct is installed.

Your role is not to invent a new sprinkler location.

Document condition → compare approved coordinated drawings → notify Responsable qualité → coordinate fire-protection/mechanical teams → obtain authorized resolution → implement → inspect physical correction → obtain required specialist verification → close.

10.8.9 VERIFICATION

Confirm:

- physical correction;

- affected interfaces;

- required retest;

- specialist acceptance.

10.8.10 CLOSURE

☐ approved materials
☐ piping complete
☐ supports complete
☐ heads/devices complete
☐ valves accessible
☐ penetrations complete
☐ identification complete
☐ testing complete
☐ specialist acceptance available
☐ deficiencies closed

10.8.11 REPORTING / ANALYSIS

Track:

- open installation deficiencies;

- failed pressure tests;

- damaged heads;

- obstruction conflicts;

- missing test records;

- outstanding commissioning items.

10.8.12 QUALITY CHECKPOINT

☐ Approved drawing
☐ Pipe
☐ Fittings
☐ Routing
☐ Supports
☐ Seismic interface
☐ Heads/devices
☐ Valves
☐ Penetrations
☐ Identification
☐ Testing
☐ Specialist acceptance
☐ Closure

FIRE/LIFE-SAFETY — MASTER PRE-CONCEALMENT GATE

This should be one of the strongest STOP/CHECK gates in the whole application.

Before a wall, shaft, ceiling or enclosure closes:

RATED ASSEMBLIES

☐ Correct assembly identified
☐ Rating confirmed
☐ Required layers/components installed
☐ Concealed components inspected
☐ Perimeter/head condition complete

PENETRATIONS

☐ Every penetration identified
☐ Approved firestop system
☐ Opening/configuration acceptable
☐ Backing complete
☐ Firestop installed
☐ Penetration photographed

DAMPERS

☐ Correct damper
☐ Installation complete
☐ Access maintained
☐ Interface complete

DOORS / OPENINGS

☐ Frames installed correctly
☐ Required rated components identified
☐ Interfaces complete

MEP

☐ Mechanical penetrations complete
☐ Electrical penetrations complete
☐ Fire-protection penetrations complete

DOCUMENTATION

☐ Inspection forms
☐ Firestop register
☐ Photos
☐ NCs/deficiencies resolved or formally controlled
☐ Required hold/witness points released

If something that determines fire performance is about to disappear, that is your last inexpensive opportunity to prove it was constructed correctly.

FIRESTOP — MASTER TRACEABILITY GATE

For each controlled penetration:

WHERE IS IT?
→ penetration ID/location

WHAT ASSEMBLY?
→ wall/floor/type/rating

WHAT PASSES THROUGH IT?
→ pipe/conduit/cable/tray/duct

WHAT SYSTEM APPLIES?
→ approved/listed system reference

DO THE ACTUAL DIMENSIONS FIT THAT SYSTEM?
→ opening + penetrating item + annular space

WHAT WAS INSTALLED?
→ backing + product + depth/configuration

WHAT PROVES IT?
→ inspection + photos + label

WAS IT MODIFIED LATER?
→ reopen/reinspect if yes

That is the level of traceability I would want in our Hochelaga system.

PRACTICAL EXAMPLE — RATED WALL BEFORE DRYWALL CLOSURE

Suppose tomorrow the drywall contractor wants to close a rated electrical-room wall.

You don't simply open:

Interior → Gypsum Board

You cross-reference:

Interior → Fire-Rated Assemblies
Fire/Life Safety → Fire-Rated Walls
Fire/Life Safety → Firestopping
Mechanical → Penetrations
Electrical → Penetrations

Then:

1. Confirm wall assembly
→ correct approved wall type/rating.

2. Inspect framing/concealed components
→ studs, board layers already installed, insulation where applicable.

3. Sweep the wall physically from one end to the other.

Every:

- conduit;

- cable;

- pipe;

- duct;

- box;

- opening

gets considered.

4. Firestop register

Every controlled penetration gets status.

5. Photograph

Especially anything about to disappear.

6. Check open deficiencies

No unresolved item casually disappears behind drywall.

7. Release according to CRT's actual project procedure.

Now you have controlled the assembly, not merely inspected some drywall.

PRACTICAL EXAMPLE — THE DANGEROUS “SMALL CHANGE”

Three weeks later an electrician adds one conduit through that already accepted wall.

Visually, it is tiny.

From a QMS perspective:

The previously accepted rated assembly has been modified.

So:

new penetration → identify rated wall → establish applicable approved firestop system → inspect installation → photograph → update penetration register → restore wall's quality status

This is precisely why a systematic inspector catches things that a purely reactive inspector can miss.

10. FIRE & LIFE-SAFETY — MODULE COMPLETE

10.1 Fire-Rated Walls ✓
10.2 Fire-Rated Floors/Ceilings ✓
10.3 Firestopping ✓✓ — high-control item
10.4 Fire/Smoke Dampers ✓
10.5 Fire-Rated Doors ✓
10.6 Fire Alarm Physical Installation Interfaces ✓
10.7 Emergency/Life-Safety Interfaces ✓
10.8 Fire Protection Systems ✓

And we're now seeing something important about the architecture of the eventual Hochelaga QMS: the sections should not operate as isolated checklists.

The real power will come from cross-system gates. A ceiling cannot simply be “Architectural complete”; its closure can depend on mechanical testing, electrical concealed work, firestopping, dampers, insulation and deficiencies. Likewise, a concrete pour can depend on structural reinforcement, embeds, sleeves, grounding components and electrical conduits.

That cross-referencing is what will eventually turn what we're building from a collection of inspection notes into an actual field-quality decision system.

Yes. This section is crucial, because many expensive field problems are not failures of one trade’s workmanship; they are failures of coordination between systems.

At Hochelaga, that risk is even higher because the building work has to coexist with substantial electrical equipment, conduits, cable trays, grounding, HVAC, structural supports, penetrations, fire separations, equipment bases, and maintenance clearances.

The governing principle for this module is:

No interface is considered complete just because each trade completed its own scope. The interface is complete only when the combined condition works physically, technically, and functionally across all affected disciplines.

The universal interface workflow is:

Identify interface → identify all affected disciplines → establish governing documents → coordinate sequence → inspect prerequisites → inspect physical interface → verify concealed conditions → document → resolve conflicts → verify correction → close interface

11. MULTIDISCIPLINARY INTERFACES

Overall quality objective

Ensure adjacent or overlapping systems are physically compatible, correctly sequenced, structurally supported, accessible, protected, sealed and coordinated so that completion of one trade does not compromise another trade or the building as a whole.

The quality questions become:

Who touches this condition?
Whose drawing governs what part?
What happens first?
What becomes hidden?
Can the final assembled condition actually work?

11.1 STRUCTURAL ↔ ARCHITECTURAL

Quality objective

Ensure architectural systems connect to and depend upon structural construction without dimensional conflicts, unsupported conditions, improper penetrations or compromised architectural performance.

Typical interfaces include:

- wall framing to structure;

- masonry to structure;

- curtain/cladding supports;

- roof/parapet interfaces;

- door openings;

- slab edges;

- stairs;

- architectural embeds;

- ceilings;

- fire-rated wall terminations.

11.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- structural drawings;

- architectural plans;

- wall sections;

- slab-edge details;

- wall support details;

- elevations;

- door/window openings;

- cladding shop drawings;

- masonry details;

- approved embeds;

- fire-rated assembly details;

- movement-joint details;

- Plan Qualité;

- PIE/PRIE;

- technical changes;

- QMT/RFI responses.

Extract:

- structural geometry;

- architectural finished dimensions;

- tolerances;

- anchor locations;

- edge conditions;

- movement allowances;

- openings;

- embeds;

- finish build-ups.

11.1.2 PLANNING

Before architectural work begins:

- compare structural as-built condition against architectural requirements;

- identify openings;

- identify support locations;

- identify embeds/anchors;

- coordinate tolerances;

- inspect conditions before finishes hide structure.

Typical question

Does the actual structure provide the location, dimension and support the architectural system expects?

11.1.3 DOCUMENT CONTROL

Verify:

☐ structural revision
☐ architectural revision
☐ approved shop drawings
☐ as-built/survey where relevant
☐ technical changes aligned across disciplines

A structural revision that moves an opening is meaningless if the architectural trade is still building from the old plan.

11.1.4 MATERIAL CONTROL

Check interface components:

- anchors;

- clips;

- embeds;

- backing;

- shelf angles;

- connection plates;

- shims;

- sealants;

- isolation materials.

11.1.5 INSPECTION

Check:

- slab edge/location;

- wall-to-structure alignment;

- support conditions;

- door/opening dimensions;

- cladding/masonry anchors;

- deflection/movement details;

- ceiling supports;

- fire-rated top-of-wall conditions.

Watch for

- wall built below structural opening incorrectly;

- architectural wall forced around structural misalignment;

- unauthorized field trimming;

- missing support;

- architectural system rigidly connected where movement is required.

11.1.6 RECORDS / EVIDENCE

Capture:

- interface location;

- structural reference;

- architectural reference;

- measurements;

- photos;

- conflict/disposition;

- correction;

- final accepted condition.

11.1.7 NC / DEFICIENCY

Typical:

- opening wrong size;

- slab edge mislocated;

- missing embed;

- wall unsupported;

- incorrect movement interface;

- architectural finish unable to achieve required geometry.

11.1.8 CORRECTIVE ACTION — EXAMPLE

Structural opening is 60 mm narrower than required architectural door assembly.

Measure → confirm both drawings → document conflict → prevent frame installation → coordinate structural/architectural professional disposition → implement approved correction → remeasure → inspect frame installation afterward → close.

11.1.9 VERIFICATION

Confirm both sides of interface remain compliant after correction.

11.1.10 CLOSURE

☐ structural condition accepted
☐ architectural requirement accepted
☐ interface components complete
☐ movement/support correct
☐ downstream finish can proceed
☐ records complete

11.1.11 REPORTING / ANALYSIS

Track recurring dimensional conflicts between structural and architectural documentation or installation.

11.1.12 QUALITY CHECKPOINT

☐ Structural geometry
☐ Architectural geometry
☐ Opening
☐ Support
☐ Anchors/embeds
☐ Movement detail
☐ Fire interface
☐ Finish interface
☐ Final coordination

11.2 STRUCTURAL ↔ MECHANICAL

Quality objective

Ensure mechanical systems are supported and routed without compromising structural elements, while structural construction incorporates all required openings, embeds, sleeves, pads and supports.

Typical interfaces:

- pipe/duct penetrations;

- equipment bases;

- hangers;

- sleeves;

- openings;

- roof curbs;

- housekeeping pads;

- structural supports for equipment;

- vibration-isolation interfaces.

11.2.1 REQUIREMENTS

Obtain:

- structural drawings;

- mechanical drawings;

- equipment shop drawings;

- penetration/opening drawings;

- support details;

- equipment loads where relevant;

- base/pad details;

- coordination drawings;

- approved hanger details;

- structural professional directives;

- PIE/PRIE.

11.2.2 PLANNING

Before concrete/steel closes:

- identify all mechanical openings;

- identify sleeves;

- identify embeds;

- identify equipment bases;

- identify support loads;

- coordinate large duct/pipe crossings;

- identify areas where coring later would be undesirable.

High-value rule

Solve penetrations before concrete wherever possible.

11.2.3 DOCUMENT CONTROL

Verify:

☐ latest structural drawing
☐ latest mechanical layout
☐ approved equipment dimensions
☐ opening/sleeve schedule
☐ support detail
☐ coordination model/drawing current

11.2.4 MATERIAL CONTROL

Check:

- sleeves;

- anchors;

- inserts;

- supports;

- housekeeping-pad materials;

- vibration isolators;

- curbs;

- structural support steel.

11.2.5 INSPECTION

Check:

- opening location;

- opening dimensions;

- sleeve;

- embed;

- support;

- equipment base;

- anchorage;

- no unauthorized cutting/drilling;

- no interference with reinforcement/steel;

- mechanical route fits actual structural geometry.

11.2.6 RECORDS

Capture:

- opening ID;

- equipment/system;

- structural element;

- dimensions;

- pre-pour photos;

- support;

- correction/disposition.

11.2.7 NC / DEFICIENCY

Typical:

- mechanical sleeve missing;

- duct opening too small;

- pipe clashes with beam;

- hanger attached to prohibited structural element;

- housekeeping pad wrong size;

- unauthorized core drilling.

11.2.8 CORRECTIVE ACTION — EXAMPLE

Large duct conflicts with structural beam.

Do not allow field crews to simply notch, cut or reroute structural work.

Identify clash → document actual condition → compare coordinated drawings → notify mechanical + structural parties + Responsable qualité → obtain authorized resolution → implement → inspect both systems → close.

11.2.9 VERIFICATION

Confirm:

- structure unaffected/accepted;

- mechanical system fits;

- support/access maintained;

- fire/envelope interfaces restored if involved.

11.2.10 CLOSURE

☐ openings correct
☐ structural support accepted
☐ mechanical route accepted
☐ anchors/supports complete
☐ equipment bases complete
☐ no unresolved clash

11.2.11 REPORTING / ANALYSIS

Track repeated late penetrations or coordination failures.

11.2.12 QUALITY CHECKPOINT

☐ Structure
☐ Mechanical route
☐ Opening
☐ Sleeve
☐ Support
☐ Anchor
☐ Equipment base
☐ Access
☐ No unauthorized structural modification

11.3 STRUCTURAL ↔ ELECTRICAL

Quality objective

Ensure electrical raceways, cable trays, equipment, grounding interfaces and embedded components are coordinated with structural construction without unauthorized structural modification or misplaced electrical infrastructure.

This is particularly important on Hochelaga.

11.3.1 REQUIREMENTS

Obtain:

- structural drawings;

- electrical plans;

- conduit/duct-bank drawings;

- equipment layouts;

- cable-tray layouts;

- grounding drawings;

- embedded conduit drawings;

- equipment base details;

- anchor-bolt drawings;

- penetration drawings;

- coordination drawings;

- PIE/PRIE.

11.3.2 PLANNING

Before structural work:

- identify embedded conduits;

- electrical stub-ups;

- grounding components;

- equipment anchors;

- cable-tray supports;

- wall/slab openings;

- large electrical equipment bases.

11.3.3 DOCUMENT CONTROL

Verify:

☐ current structural drawing
☐ current electrical drawing
☐ current equipment layout
☐ embed/stub-up detail
☐ coordination drawing
☐ technical changes aligned

11.3.4 MATERIAL CONTROL

Check:

- conduits;

- inserts;

- sleeves;

- anchors;

- grounding components;

- embedded plates;

- support steel.

11.3.5 INSPECTION

Before concrete:

- conduit size/location;

- stub-ups;

- anchor bolts;

- grounding components;

- sleeves;

- clearance from reinforcement;

- secure fixing.

After structural work:

- actual equipment footprint;

- cable-tray route;

- anchor locations;

- wall/floor openings;

- no unauthorized coring/cutting.

11.3.6 RECORDS

Capture strong pre-pour evidence because embedded electrical work disappears permanently.

11.3.7 NC / DEFICIENCY

Typical:

- misplaced electrical stub-up;

- missing grounding embed;

- tray conflict with beam;

- equipment anchors misplaced;

- unapproved structural drilling.

11.3.8 CORRECTIVE ACTION — EXAMPLE

Conduit bank stub-ups emerge inside future equipment base rather than connection zone.

Survey → document → compare equipment/shop drawings → stop pad/equipment progression → authorized electrical/structural coordination → approved correction → verify → close.

11.3.9 VERIFICATION

Cross-check final physical condition against both structural and electrical requirements.

11.3.10 CLOSURE

☐ embedded electrical accepted
☐ structural condition accepted
☐ equipment interface correct
☐ openings/supports complete
☐ documentation complete

11.3.11 REPORTING / ANALYSIS

Track missed embeds/stub-ups especially because repeated errors can be very costly.

11.3.12 QUALITY CHECKPOINT

☐ Conduits
☐ Stub-ups
☐ Grounding embeds
☐ Anchor bolts
☐ Openings
☐ Cable tray supports
☐ Equipment footprint
☐ Structure unaffected
☐ Pre-concealment evidence

11.4 ENVELOPE ↔ MECHANICAL

Quality objective

Ensure mechanical systems cross or connect to the building envelope without compromising water, air, vapour or thermal performance.

Examples:

- exterior duct penetration;

- intake/exhaust louvres;

- roof pipes;

- rooftop equipment;

- wall-mounted mechanical equipment;

- drains;

- exhaust terminations.

11.4.1 REQUIREMENTS

Obtain:

- envelope details;

- mechanical drawings;

- penetration details;

- louvre shop drawings;

- roof details;

- air-barrier details;

- waterproofing/flashing;

- insulation details;

- curb details;

- manufacturer instructions;

- PIE/PRIE.

11.4.2 PLANNING

Coordinate before envelope closure:

- opening;

- sleeve;

- curb/louvre;

- mechanical connection;

- flashing;

- membrane transitions;

- insulation;

- sealant;

- drainage.

11.4.3 DOCUMENT CONTROL

Verify:

☐ mechanical location
☐ envelope detail
☐ approved opening
☐ flashing detail
☐ current air/water seal detail

11.4.4 MATERIAL CONTROL

Check:

- sleeves;

- curbs;

- flashings;

- membranes;

- sealants;

- insulation;

- louvres;

- boots/collars.

11.4.5 INSPECTION

Check:

- opening size;

- sleeve;

- mechanical component;

- water-shedding geometry;

- air barrier continuity;

- vapour control;

- thermal insulation;

- flashing;

- sealant;

- drainage;

- no membrane damage.

11.4.6 RECORDS

Capture:

- penetration/interface ID;

- before/after membrane;

- flashing;

- insulation;

- completed service.

11.4.7 NC / DEFICIENCY

Common:

- unsealed duct penetration;

- missing flashing;

- insulation gap;

- air barrier cut;

- roof pipe poorly flashed;

- louvre perimeter incomplete.

11.4.8 CORRECTIVE ACTION — EXAMPLE

Mechanical exhaust penetration is installed after air barrier, leaving torn membrane around sleeve.

Stop local concealment → verify approved detail → restore substrate/membrane → install transition/flashing → complete mechanical connection → reinspect → photograph → close.

11.4.9 VERIFICATION

Check full control-layer continuity.

11.4.10 CLOSURE

☐ mechanical installation complete
☐ air barrier restored
☐ waterproofing/flashing complete
☐ insulation complete
☐ sealants complete
☐ evidence captured

11.4.11 REPORTING / ANALYSIS

Track envelope damage by MEP trades.

11.4.12 QUALITY CHECKPOINT

☐ Opening
☐ Sleeve/curb
☐ Mechanical component
☐ Air barrier
☐ Vapour control
☐ Insulation
☐ Flashing
☐ Sealant
☐ Drainage
☐ Evidence

11.5 ENVELOPE ↔ ELECTRICAL

Quality objective

Ensure electrical services penetrate or mount to the envelope without compromising air, water, vapour and thermal continuity.

Examples:

- conduits;

- cable trays;

- exterior equipment;

- wall boxes;

- roof penetrations;

- exterior lighting;

- grounding interfaces.

11.5.1 REQUIREMENTS

Obtain:

- electrical drawings;

- envelope details;

- roof/wall penetration details;

- air-barrier details;

- flashing details;

- approved exterior equipment/shop drawings;

- PIE/PRIE.

11.5.2 PLANNING

Identify all envelope electrical penetrations before membrane/cladding installation.

11.5.3 DOCUMENT CONTROL

Verify:

☐ electrical route
☐ opening location
☐ envelope detail
☐ flashing/seal system
☐ latest changes

11.5.4 MATERIAL CONTROL

Check:

- sleeves;

- boots;

- collars;

- sealants;

- flashings;

- membrane patches;

- insulation.

11.5.5 INSPECTION

Check:

- opening;

- sleeve;

- conduit/tray;

- support;

- air seal;

- water seal;

- insulation;

- flashing;

- sealant;

- exterior equipment mounting.

11.5.6 RECORDS

Photograph before cladding/roof completion.

11.5.7 NC / DEFICIENCY

Typical:

- membrane punctured;

- conduit sealed only with generic caulk;

- missing flashing;

- thermal gap;

- unplanned roof penetration.

11.5.8 CORRECTIVE ACTION

Restore full envelope assembly per approved detail.

11.5.9 VERIFICATION

Confirm all control layers restored.

11.5.10 CLOSURE

☐ electrical interface accepted
☐ envelope continuity restored
☐ evidence complete

11.5.11 REPORTING / ANALYSIS

Track repeated late penetrations.

11.5.12 QUALITY CHECKPOINT

☐ Opening
☐ Electrical service
☐ Air seal
☐ Water seal
☐ Vapour layer
☐ Insulation
☐ Flashing
☐ Sealant
☐ Support
☐ Evidence

11.6 ARCHITECTURAL ↔ MEP

This is one of the most common coordination zones.

Quality objective

Ensure MEP installations integrate into architectural walls, ceilings, floors, doors and finishes without compromising appearance, fire/acoustic performance, access or functionality.

Examples:

- diffusers in ceilings;

- lights;

- sprinklers;

- detectors;

- electrical boxes;

- pipe penetrations;

- access panels;

- floor drains;

- wall-mounted equipment.

11.6.1 REQUIREMENTS

Obtain:

- architectural plans;

- reflected ceiling plans;

- mechanical layouts;

- electrical layouts;

- fire-protection drawings;

- coordination drawings;

- room elevations;

- equipment/shop drawings;

- access requirements;

- PIE/PRIE.

11.6.2 PLANNING

Before walls/ceilings close:

- coordinate device locations;

- identify access requirements;

- identify backing;

- identify penetrations;

- resolve visible alignment issues.

11.6.3 DOCUMENT CONTROL

Verify current:

☐ RCP
☐ MEP plans
☐ wall elevations
☐ equipment dimensions
☐ access panel requirements

11.6.4 MATERIAL CONTROL

Check interface hardware:

- supports;

- trim;

- escutcheons;

- access panels;

- boxes;

- mounting plates.

11.6.5 INSPECTION

Check:

Ceilings

- diffuser alignment;

- light alignment;

- sprinkler/device positions;

- access panels;

- no clashes.

Walls

- switches/outlets;

- controls;

- pipe/conduit penetrations;

- equipment;

- backing;

- finish around openings.

Floors

- drains;

- sleeves;

- equipment bases;

- finish interfaces.

Access

Verify maintainability after finishes.

11.6.6 RECORDS

Capture congested/critical areas before closure and final appearance afterward.

11.6.7 NC / DEFICIENCY

Common:

- light and diffuser clash;

- access panel missing;

- switch hidden by equipment;

- pipe penetration poorly finished;

- device not aligned with architectural layout.

11.6.8 CORRECTIVE ACTION — EXAMPLE

Ceiling layout places diffuser directly where light fixture is scheduled.

Identify conflict before grid closure → compare coordinated drawings → resolve with architectural/MEP team → install revised arrangement → inspect appearance/function → document.

11.6.9 VERIFICATION

Check both functional and architectural outcomes.

11.6.10 CLOSURE

☐ MEP complete
☐ architecture complete
☐ devices aligned
☐ access maintained
☐ finishes restored
☐ no unresolved clashes

11.6.11 REPORTING / ANALYSIS

Track recurrent coordination issues by room/zone.

11.6.12 QUALITY CHECKPOINT

☐ Walls
☐ Ceilings
☐ Floors
☐ Device locations
☐ Backing
☐ Access panels
☐ Penetrations
☐ Finish quality
☐ Maintainability

11.7 PENETRATIONS — UNIVERSAL WORKFLOW

This should become one of the most useful universal modules.

The sequence is:

Opening → sleeve → service → structural condition → waterproofing/air barrier → insulation → firestop → architectural finish → identification → closure

Quality objective

Manage every penetration as a multidisciplinary assembly rather than as merely a hole through a wall/floor/roof.

11.7.1 REQUIREMENTS

For every penetration, establish:

- location;

- host assembly;

- structural requirement;

- service;

- opening dimensions;

- sleeve;

- fire rating;

- envelope requirement;

- acoustic requirement;

- insulation requirement;

- finish;

- approved details.

11.7.2 PLANNING

Ideally assign penetration ID.

Determine:

- who creates opening;

- who installs sleeve;

- who installs service;

- who restores envelope;

- who firestops;

- who finishes;

- who inspects each stage.

That ownership map prevents:

“I thought the other trade was doing it.”

11.7.3 DOCUMENT CONTROL

Cross-check:

☐ architectural
☐ structural
☐ mechanical/electrical
☐ firestop
☐ envelope detail
☐ technical changes

11.7.4 MATERIAL CONTROL

Check:

- sleeve;

- sealants;

- membranes;

- firestop;

- insulation;

- finish accessories.

11.7.5 INSPECTION — UNIVERSAL SEQUENCE

Step 1 — Opening

☐ location
☐ size
☐ structure unaffected/approved

Step 2 — Sleeve

☐ correct type
☐ position
☐ projection
☐ secure

Step 3 — Service

☐ correct service
☐ clearance
☐ support

Step 4 — Envelope

Where applicable:
☐ air barrier
☐ vapour layer
☐ waterproofing
☐ flashing

Step 5 — Insulation

☐ thermal/acoustic continuity restored

Step 6 — Firestop

Where rated:
☐ approved system
☐ dimensions
☐ backing
☐ product
☐ depth

Step 7 — Finish

☐ escutcheon/trim
☐ wall/ceiling finish restored

11.7.6 RECORDS

A penetration record can include:

ID → location → host assembly → service → approved detail → photos at stages → firestop → finish → status

11.7.7 NC / DEFICIENCY

Any incomplete stage can make penetration quality incomplete.

11.7.8 CORRECTIVE ACTION

Correct appropriate layer without compromising others.

11.7.9 VERIFICATION

Inspect entire penetration assembly after repair, not merely the repaired layer.

11.7.10 CLOSURE

☐ opening
☐ sleeve
☐ service
☐ structure
☐ envelope
☐ insulation
☐ firestop
☐ finish
☐ evidence

Only then:

PENETRATION CLOSED

11.8 EMBEDDED ITEMS

Quality objective

Ensure every cast-in item required by another discipline is correctly identified, coordinated, positioned and secured before concrete permanently conceals it.

Examples:

- sleeves;

- anchor bolts;

- inserts;

- grounding;

- conduits;

- plates;

- drains;

- embedded supports.

11.8.1 REQUIREMENTS

Cross-check:

- structural;

- mechanical;

- electrical;

- architectural;

- equipment shop drawings;

- embed schedules;

- coordination drawings.

11.8.2 PLANNING

Before pour, perform a multidisciplinary embed walkdown.

Representatives or information from:

structure + mechanical + electrical + architectural/equipment

must be accounted for.

11.8.3 DOCUMENT CONTROL

Verify all relevant drawings are current.

11.8.4 MATERIAL CONTROL

Check embedded component approvals and condition.

11.8.5 INSPECTION

Check:

- component;

- location;

- elevation;

- orientation;

- projection;

- anchorage;

- interference;

- secure fixing.

11.8.6 RECORDS

Capture pre-pour photos and measured locations.

11.8.7 NC / DEFICIENCY

Typical:

- missing sleeve;

- misplaced bolt;

- wrong conduit;

- missing insert;

- uncoordinated embed.

11.8.8 CORRECTIVE ACTION

Best time is before concrete.

Correct → reinspect → photograph.

11.8.9 VERIFICATION

Perform final embed walkdown before pour release.

11.8.10 CLOSURE

☐ all disciplines accounted for
☐ embeds installed
☐ locations verified
☐ conflicts resolved
☐ evidence complete

11.8.11 REPORTING / ANALYSIS

Track missed embeds because they often indicate coordination breakdown.

11.8.12 QUALITY CHECKPOINT

☐ Structural
☐ Mechanical
☐ Electrical
☐ Architectural
☐ Equipment
☐ Location
☐ Elevation
☐ Orientation
☐ Secure
☐ Pre-pour evidence

11.9 EQUIPMENT BASES / HOUSEKEEPING PADS

Quality objective

Provide correctly sized, positioned and elevated structural bases that match approved equipment, anchor patterns, service connections, vibration requirements and maintenance clearances.

11.9.1 REQUIREMENTS

Obtain:

- equipment shop drawing;

- architectural/mechanical/electrical layout;

- structural base detail;

- anchor details;

- pad dimensions;

- elevation;

- grout requirement;

- vibration-isolation requirements;

- equipment clearances.

11.9.2 PLANNING

Before pad pour:

- verify final equipment model;

- footprint;

- anchor pattern;

- conduit/pipe stub-ups;

- orientation;

- access;

- vibration isolation.

11.9.3 DOCUMENT CONTROL

☐ equipment shop drawing
☐ base detail
☐ anchor pattern
☐ latest service locations

11.9.4 MATERIAL CONTROL

Check:

- concrete;

- reinforcement;

- anchors;

- grout;

- isolators;

- embedded items.

11.9.5 INSPECTION

Before pour

- location;

- dimensions;

- elevation;

- reinforcement;

- anchors;

- conduits;

- sleeves.

After pour

- dimensions;

- level;

- surface;

- anchor position;

- defects.

Equipment installation

- equipment fits;

- orientation correct;

- service connections align;

- maintenance clearance remains.

11.9.6 RECORDS

Capture pad ID, equipment ID, pre-pour and post-pour evidence.

11.9.7 NC / DEFICIENCY

Common:

- pad wrong size;

- anchor mismatch;

- wrong elevation;

- equipment cannot fit;

- conduit emerges under frame;

- insufficient service clearance.

11.9.8 CORRECTIVE ACTION — EXAMPLE

Housekeeping pad correct structurally but 150 mm too close to wall, eliminating equipment maintenance clearance.

This is still a quality problem.

Document → coordinate disposition → correct base/equipment arrangement as authorized → verify maintainability.

11.9.9 VERIFICATION

Confirm equipment physically fits and can be serviced.

11.9.10 CLOSURE

☐ pad correct
☐ anchors correct
☐ equipment fits
☐ services align
☐ access maintained
☐ records complete

11.9.11 REPORTING / ANALYSIS

Track pad/equipment coordination failures.

11.9.12 QUALITY CHECKPOINT

☐ Equipment ID
☐ Footprint
☐ Pad dimensions
☐ Elevation
☐ Anchors
☐ Stub-ups
☐ Surface
☐ Equipment orientation
☐ Service clearances

11.10 ACCESS & MAINTAINABILITY

This is a very high-value QC module because a technically functioning system can still be badly constructed if nobody can maintain it.

Quality objective

Ensure installed equipment, valves, dampers, filters, panels, controls and service components remain practically accessible for inspection, operation, removal and maintenance after construction is complete.

11.10.1 REQUIREMENTS

Obtain:

- manufacturer service-clearance requirements;

- equipment shop drawings;

- architectural room layouts;

- mechanical/electrical layouts;

- access-panel requirements;

- O&M requirements;

- applicable code/project clearances;

- coordination drawings.

11.10.2 PLANNING

For every major item ask before installation:

How will this be maintained?

What must be removed someday?

What direction does the service panel open?

Can the filter/motor/coil/breaker/valve actually be reached?

11.10.3 DOCUMENT CONTROL

Verify:

☐ manufacturer clearance
☐ equipment orientation
☐ access-panel location
☐ room/layout current

11.10.4 MATERIAL CONTROL

Where applicable:

- access panels;

- removable panels;

- service platforms;

- ladders;

- guards.

11.10.5 INSPECTION

Physically check:

Equipment

- doors open;

- panels removable;

- filters removable;

- motors accessible;

- electrical clearances maintained.

Valves

- reachable;

- operable.

Dampers

- accessible for inspection/reset.

Above ceiling

- access panel actually aligns with service item.

Removal path

For major components, consider whether replacement/removal is physically possible as required by approved design.

11.10.6 RECORDS

Capture critical equipment clearances and access panels.

11.10.7 NC / DEFICIENCY

Common:

- equipment blocked by pipe;

- filter cannot be removed;

- valve inaccessible;

- access panel offset from damper;

- panel door blocked by wall/equipment.

11.10.8 CORRECTIVE ACTION — EXAMPLE

Valve located above drywall ceiling without access panel.

Identify valve → verify access requirement → coordinate panel → install → physically test ability to reach/operate valve → close.

11.10.9 VERIFICATION

Don't just see the panel.

Open it and verify actual access.

11.10.10 CLOSURE

☐ service clearance
☐ operational access
☐ removable components accessible
☐ access panels complete
☐ maintenance path viable
☐ evidence complete

11.10.11 REPORTING / ANALYSIS

Track maintainability issues by room/system because many arise from congestion.

11.10.12 QUALITY CHECKPOINT

☐ Equipment doors
☐ Panels
☐ Filters
☐ Motors
☐ Valves
☐ Dampers
☐ Controls
☐ Access panels
☐ Removal path
☐ Maintenance clearance

11.11 TRADE COORDINATION / CONGESTION

This could become one of the most useful daily field modules at Hochelaga.

Quality objective

Identify and resolve physical conflicts among structural, architectural, mechanical, electrical and fire-protection systems before they create field improvisation, rework or inaccessible construction.

11.11.1 REQUIREMENTS

Obtain:

- all current discipline drawings;

- approved shop drawings;

- coordination drawings/BIM;

- equipment layouts;

- reflected ceiling plans;

- structural details;

- service clearances;

- access requirements;

- technical changes;

- RFI/QMT responses.

11.11.2 PLANNING

Focus on congestion zones:

- electrical rooms;

- mechanical rooms;

- ceiling corridors;

- shafts;

- roof equipment areas;

- wall penetrations;

- equipment entrances;

- underground service zones.

Before installation, conduct a coordination walkdown.

Ask:

What gets installed first?

What physically has the least flexibility?

Usually large structural elements, major ducts, cable trays, gravity drainage and large equipment have fewer routing options than small conduits.

But actual sequencing must follow project coordination.

11.11.3 DOCUMENT CONTROL

A coordinated installation requires all disciplines to be using current information.

Check revision alignment.

11.11.4 MATERIAL CONTROL

Generally system-specific, but confirm major equipment dimensions because coordination based on wrong equipment dimensions is useless.

11.11.5 INSPECTION / COORDINATION

Look for:

- physical clashes;

- insufficient clearance;

- inaccessible valves/dampers;

- impossible cable pull paths;

- ceiling congestion;

- incompatible support systems;

- competing penetration locations;

- equipment removal obstruction;

- drainage slope conflicts;

- duct/tray hierarchy issues.

Three-dimensional thinking

Don't only inspect plan-view location.

Think:

X → Y → Z

Horizontal location + elevation + future access.

11.11.6 RECORDS / EVIDENCE

For a conflict record:

- exact location;

- systems involved;

- current drawings;

- photographs;

- measurements;

- impact;

- required decision;

- agreed resolution;

- responsible parties;

- status.

11.11.7 NC / DEFICIENCY

A coordination issue may become:

- deficiency;

- RFI/QMT;

- design clarification;

- NCR;

- change;

depending on cause and project procedure.

Do not force every clash into an NCR.

11.11.8 CORRECTIVE ACTION — EXAMPLE

Cable tray, sprinkler main and HVAC duct all occupy same ceiling zone.

Poor field response:

“First guy there wins.”

😂

Quality-system response:

Document clash → identify approved coordination drawings → determine which installation deviated / whether design conflict exists → coordinate responsible disciplines → obtain authorized resolution → revise installation sequence → implement → inspect → update records.

11.11.9 VERIFICATION

After resolution:

- all affected systems fit;

- clearances maintained;

- slopes preserved;

- supports complete;

- access maintained;

- fire/envelope interfaces complete.

11.11.10 CLOSURE

☐ conflict resolved
☐ authorized arrangement
☐ all trades coordinated
☐ access maintained
☐ no new downstream conflict
☐ documentation updated

11.11.11 REPORTING / ANALYSIS

This section is perfect for trend analysis.

Track:

- clash type;

- discipline pair;

- zone;

- root cause;

- drawing revision;

- rework hours if known;

- resolution time.

If repeatedly:

Electrical ↔ Mechanical = conflict

in the same type of corridor, your quality contribution becomes:

“We're seeing a recurring coordination pattern. Let's address the next zones before installation rather than after.”

That's the move from inspector to anticipatory quality management.

11.11.12 TRADE COORDINATION QUALITY CHECKPOINT

Before closing a congested zone:

STRUCTURE

☐ No unauthorized cuts/drilling
☐ Supports coordinated

MECHANICAL

☐ Ducts
☐ Pipes
☐ Slopes
☐ Valves
☐ Access

ELECTRICAL

☐ Cable trays
☐ Conduits
☐ Equipment clearance
☐ Pull/access paths

FIRE PROTECTION

☐ Piping/heads
☐ Dampers
☐ Firestop

ARCHITECTURAL

☐ Ceiling elevation
☐ Wall location
☐ Access panels
☐ Finish clearances

MAINTAINABILITY

☐ Equipment accessible
☐ Valves accessible
☐ Dampers accessible
☐ Panels accessible

DOCUMENTATION

☐ Current coordination drawings
☐ Changes captured
☐ Conflicts resolved
☐ Photos complete

MULTIDISCIPLINARY INTERFACE — MASTER DAILY WORKFLOW

This could eventually be a dedicated button:

INTERFACE CHECK

Whenever you encounter a complex condition:

1. IDENTIFY

What physical condition am I looking at?

2. DISCIPLINES

Who is involved?

☐ Structural
☐ Architectural
☐ Mechanical
☐ Electrical
☐ Fire protection
☐ Envelope

3. DOCUMENTS

What does each discipline require?

4. SEQUENCE

Who has to work first?

5. CONCEALMENT

What will become inaccessible?

6. PERFORMANCE

Could one system compromise another?

- structure;

- waterproofing;

- air barrier;

- fire rating;

- insulation;

- drainage;

- operation;

- maintenance.

7. ACCESS

Can it still be maintained?

8. EVIDENCE

Have I captured what will disappear?

9. CONFLICT?

If yes:

CONTROL → DOCUMENT → COORDINATE → AUTHORIZED RESOLUTION → IMPLEMENT → VERIFY

10. CLOSE

Only after all affected disciplines are satisfactory.

PRACTICAL EXAMPLE — HOCHELAGA ELECTRICAL ROOM

Imagine a high-density equipment room.

You have:

- major electrical cabinets;

- cable trays;

- conduits;

- HVAC duct;

- fire-protection piping;

- fire-rated walls;

- equipment pads;

- grounding;

- penetrations.

A weak QC approach inspects each trade independently:

Steel ✓
Duct ✓
Tray ✓
Wall ✓

But the room can still be a disaster.

Your interface system asks:

Can cabinet doors open?

Can cables actually enter equipment?

Can filters/dampers be maintained?

Are cable trays blocking sprinkler devices?

Did conduits compromise the rated wall?

Does ductwork interfere with electrical clearances?

Does the equipment fit its pad?

Are penetrations properly firestopped?

Can equipment be removed later?

That's much closer to how a quality manager thinks about the finished facility.

11. MULTIDISCIPLINARY INTERFACES — MODULE COMPLETE

11.1 Structural ↔ Architectural ✓
11.2 Structural ↔ Mechanical ✓
11.3 Structural ↔ Electrical ✓
11.4 Envelope ↔ Mechanical ✓
11.5 Envelope ↔ Electrical ✓
11.6 Architectural ↔ MEP ✓
11.7 Universal Penetrations ✓✓
11.8 Embedded Items ✓
11.9 Equipment Bases/Housekeeping Pads ✓
11.10 Access & Maintainability ✓✓
11.11 Trade Coordination / Congestion ✓✓

And I would mark three modules as particularly valuable for your daily Hochelaga work:

11.7 Penetrations — because virtually every discipline creates them.

11.10 Access & Maintainability — because trades often focus on installation rather than final operability.

11.11 Coordination/Congestion — because the electrical/mechanical intensity of a substation building makes interfaces unusually important.

This is also the section that starts pushing the system beyond “How do I inspect?” into “How do I anticipate project-wide quality problems before they happen?” — exactly the kind of shift that would support greater responsibility later.

NB: WOULD BE GOOD TO HAVE INTER APP/INTERFACE LINKS TO FACILITATE THE MULTI-DISCIPLINARY APPROACH

Yes. External Works should use the same field-execution logic, but the quality emphasis shifts toward:

survey/layout → buried-work traceability → approved materials → slopes/elevations → compaction → drainage → interfaces → pre-concealment evidence → final restoration

The governing principle remains:

CRT/Hydro-Québec drawings, devis, Plan Qualité, PIE/PRIE, approved shop drawings, geotechnical requirements, municipal/site standards, technical directives, and applicable project requirements govern.

12. EXTERNAL WORKS

Overall quality objective

Ensure exterior civil/site systems are installed in the correct location and elevation, using approved materials and proper installation methods, with concealed work fully documented, tested where required, and completed so drainage, access, durability and final site performance are achieved.

The universal external-works workflow is:

Survey/layout → excavation → bedding/subgrade → material verification → installation → testing/inspection → pre-concealment evidence → backfill/compaction → final elevation/slope → surface restoration → closure

12.1 UNDERGROUND SERVICES

Quality objective

Install underground utility systems in the correct location, elevation and configuration, using approved materials, with proper bedding, joints, protection, identification, testing, backfill and as-built traceability.

Examples may include:

- water;

- sanitary;

- storm;

- electrical duct banks;

- telecom;

- grounding;

- fire-protection services;

- other site utilities.

12.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- civil utility plans;

- profiles;

- utility schedules;

- mechanical/electrical underground drawings;

- structural/site drawings;

- utility specifications;

- bedding/backfill details;

- separation requirements;

- approved shop drawings;

- utility-owner requirements;

- testing procedures;

- trench details;

- marker/identification requirements;

- geotechnical report;

- Plan Qualité;

- PIE/PRIE;

- technical directives;

- QMT/RFI responses.

Extract:

- service type;

- pipe/conduit material;

- size;

- route;

- invert/elevation;

- depth;

- slope where relevant;

- bedding;

- joint type;

- separation;

- insulation/protection;

- warning tape/marker;

- testing;

- backfill;

- compaction;

- as-built requirements.

12.1.2 PLANNING

Before excavation:

- confirm layout;

- locate existing utilities;

- identify crossing points;

- coordinate utility sequence;

- determine trench depth;

- identify groundwater;

- plan testing;

- identify pre-concealment inspection;

- coordinate as-built survey before backfill.

Key quality question

What information will be permanently lost after this service is buried?

At minimum:

- exact route;

- elevation;

- joints;

- crossings;

- test condition;

- service identification.

Capture before concealment.

12.1.3 DOCUMENT CONTROL

Verify:

☐ latest utility plan
☐ correct profile
☐ latest invert/elevation
☐ correct material/specification
☐ current crossing detail
☐ latest changes incorporated
☐ current PIE/PRIE

12.1.4 MATERIAL CONTROL

Check:

- pipe/conduit;

- fittings;

- gaskets;

- couplings;

- chambers/boxes;

- insulation;

- bedding;

- marker tape;

- tracer wire where applicable;

- coatings;

- seals;

- damaged material.

12.1.5 INSPECTION / TESTING

Route

Verify:

- correct alignment;

- crossing locations;

- separation from other services;

- interface with structures.

Elevation/depth

Check:

- invert;

- cover;

- slope where applicable.

Bedding

Verify:

- material;

- thickness;

- uniform support;

- no sharp objects;

- proper shaping where required.

Service installation

Check:

- correct material;

- size;

- joints;

- fittings;

- orientation;

- connections;

- protection.

Crossings

Inspect:

- vertical/horizontal separation;

- sleeves/protection;

- conflict resolution.

Testing

Depending on system:

- pressure;

- leak;

- continuity;

- mandrel;

- flushing;

- specialist test.

Pre-concealment

Before backfill:

☐ route documented
☐ elevation surveyed
☐ joints inspected
☐ tests passed
☐ photos taken
☐ as-built information captured

12.1.6 RECORDS / EVIDENCE

Capture:

- service ID/type;

- route;

- coordinates;

- elevations;

- joint locations;

- crossings;

- photos;

- test results;

- as-built survey;

- corrective actions;

- final connection.

12.1.7 NC / DEFICIENCY

Typical:

- wrong route;

- wrong elevation;

- wrong material;

- leaking joint;

- improper bedding;

- insufficient separation;

- damaged conduit/pipe;

- buried before testing;

- no as-built survey.

12.1.8 CORRECTIVE ACTION — EXAMPLE

Sanitary service installed 150 mm too high, creating downstream slope conflict.

Survey → identify extent → compare profile → control backfill → reset line/bedding → resurvey → retest joints/system → document → close.

12.1.9 VERIFICATION

Confirm:

- corrected route/elevation;

- bedding restored;

- joints intact;

- retest passed;

- as-built updated.

12.1.10 CLOSURE

☐ correct service
☐ correct route
☐ elevation/slope accepted
☐ bedding accepted
☐ joints accepted
☐ crossings accepted
☐ required tests passed
☐ as-built captured
☐ backfill complete
☐ identification complete

12.1.11 REPORTING / ANALYSIS

Track:

- recurring elevation errors;

- damaged utilities;

- crossing conflicts;

- repeated test failures;

- missed surveys;

- premature burial.

12.1.12 QUALITY CHECKPOINT

☐ Service type
☐ Material
☐ Size
☐ Route
☐ Elevation/depth
☐ Bedding
☐ Joints
☐ Crossings
☐ Testing
☐ As-built
☐ Photos
☐ Backfill release

12.2 UTILITY TRENCHES

Quality objective

Construct utility trenches with safe and stable geometry, suitable bottom/bedding conditions, controlled groundwater, correct service spacing, proper backfill and compaction, without damaging installed utilities.

12.2.1 REQUIREMENTS

Obtain:

- trench details;

- utility profiles;

- geotechnical requirements;

- excavation specifications;

- bedding/backfill specifications;

- shoring requirements;

- service-separation details;

- dewatering requirements;

- PIE/PRIE.

Extract:

- trench width;

- depth;

- bottom elevation;

- bedding;

- service spacing;

- backfill zones;

- lift thickness;

- compaction;

- protection.

12.2.2 PLANNING

Before digging:

- survey trench;

- locate existing utilities;

- plan excavation sequence;

- identify dewatering;

- coordinate delivery/installation;

- identify testing and survey before backfill.

12.2.3 DOCUMENT CONTROL

Verify:

☐ latest trench detail
☐ latest utility profile
☐ current service configuration
☐ current bedding/backfill criteria
☐ latest technical changes

12.2.4 MATERIAL CONTROL

Check:

- bedding;

- granular backfill;

- geotextile;

- warning tape;

- protection slabs where required.

12.2.5 INSPECTION / TESTING

Check:

Trench bottom

- elevation;

- stable condition;

- no unacceptable water;

- no unsuitable material.

Geometry

- width;

- clearance around service;

- crossing conditions.

Bedding

- correct material;

- correct thickness;

- uniform support.

Service zone

- spacing;

- support;

- no displacement.

Backfill

- correct material;

- controlled lifts;

- compaction;

- no damage to utility.

Testing

- density testing;

- service testing;

- survey.

12.2.6 RECORDS

Capture:

- trench location;

- bottom condition;

- bedding;

- service layout;

- crossings;

- as-built;

- compaction tests;

- pre-backfill photos.

12.2.7 NC / DEFICIENCY

Typical:

- poor trench bottom;

- wrong bedding;

- water accumulation;

- service displacement;

- improper spacing;

- backfill too thick per lift;

- failed compaction.

12.2.8 CORRECTIVE ACTION — EXAMPLE

Trench bottom softens after rain.

Identify affected section → remove/control water → evaluate condition against project/geotechnical requirements → remediate as authorized → reinspect → proceed with bedding only after acceptance.

12.2.9 VERIFICATION

Confirm bottom, bedding, service location, testing and compaction.

12.2.10 CLOSURE

☐ trench accepted
☐ bedding accepted
☐ services accepted
☐ testing complete
☐ as-built captured
☐ backfill compacted
☐ surface ready for restoration

12.2.11 REPORTING / ANALYSIS

Track recurring soft trench bottoms, water problems and utility damage.

12.2.12 QUALITY CHECKPOINT

☐ Layout
☐ Bottom elevation
☐ Bottom condition
☐ Bedding
☐ Service spacing
☐ Testing
☐ As-built
☐ Backfill
☐ Compaction
☐ Final surface

12.3 MANHOLES / CATCH BASINS / STRUCTURES

Quality objective

Install drainage/utility structures in the correct location and elevation, with proper base, joints, pipe connections, internal configuration, frame/grate level and final accessibility.

12.3.1 REQUIREMENTS

Obtain:

- civil plans;

- structure schedule;

- details;

- profiles;

- approved precast shop drawings;

- structure specifications;

- base/bedding details;

- pipe connections;

- watertightness requirements;

- frame/grate details;

- PIE/PRIE.

Extract:

- structure ID;

- size/type;

- invert elevations;

- pipe sizes;

- frame elevation;

- base detail;

- jointing;

- benching/channel;

- cover/grate.

12.3.2 PLANNING

Before installation:

- survey location;

- verify excavation/bottom;

- confirm incoming/outgoing pipes;

- plan crane/lifting;

- coordinate final grade/pavement elevation;

- identify test requirements.

12.3.3 DOCUMENT CONTROL

Verify:

☐ correct structure ID
☐ current profile
☐ invert elevations
☐ pipe connections
☐ frame/grate elevation
☐ current shop drawing

12.3.4 MATERIAL CONTROL

Check:

- precast sections;

- base;

- risers;

- gaskets;

- boots;

- frame;

- grate/cover;

- mortar/sealants;

- ladders/steps where applicable.

Inspect for:

- cracks;

- chips;

- damaged gasket areas;

- wrong section.

12.3.5 INSPECTION / TESTING

Base

Check:

- subgrade/bedding;

- elevation;

- level.

Structure

Check:

- plumb;

- joints;

- section alignment;

- wall condition.

Pipe connections

Check:

- invert;

- sealed connection;

- alignment.

Internal configuration

Where applicable:

- benching;

- channels;

- sump;

- cleanliness.

Frame/grate

Check:

- correct elevation;

- alignment with pavement/grade;

- secure seating.

Testing

Where specified:

- leakage;

- watertightness;

- other project tests.

12.3.6 RECORDS

Capture:

- structure ID;

- coordinates;

- invert elevations;

- internal condition;

- pipe connections;

- frame/grate;

- test results;

- photos.

12.3.7 NC / DEFICIENCY

Common:

- structure wrong location;

- wrong invert;

- leaking joint;

- cracked precast;

- poor pipe connection;

- frame too high/low;

- debris inside structure.

12.3.8 CORRECTIVE ACTION — EXAMPLE

Catch basin frame ends 25 mm above final pavement grade.

Verify final grade → survey frame → adjust risers/frame using approved method → remeasure → ensure drainage and pavement transition are correct → close.

12.3.9 VERIFICATION

Confirm location, invert, frame elevation and connection integrity.

12.3.10 CLOSURE

☐ structure correct
☐ location/elevation accepted
☐ pipe connections complete
☐ joints complete
☐ internal configuration complete
☐ frame/grate correct
☐ testing accepted
☐ records complete

12.3.11 REPORTING / ANALYSIS

Track recurring elevation and pipe-connection errors.

12.3.12 QUALITY CHECKPOINT

☐ Structure ID
☐ Location
☐ Base
☐ Inverts
☐ Pipe connections
☐ Joints
☐ Benching/channel
☐ Frame/grate
☐ Test
☐ Final grade

12.4 EXTERIOR DRAINAGE

Quality objective

Ensure exterior site grading and drainage systems direct water to intended collection points without unintended ponding, erosion, infiltration into buildings or damage to adjacent works.

12.4.1 REQUIREMENTS

Obtain:

- grading plan;

- drainage plan;

- profiles;

- catch basin locations;

- swale details;

- pavement slopes;

- building perimeter grading;

- erosion-control details;

- drainage specifications;

- PIE/PRIE.

Extract:

- finished grades;

- slopes;

- drain locations;

- invert elevations;

- swales;

- discharge points;

- tolerances.

12.4.2 PLANNING

Before final grading:

- confirm underground drainage complete;

- identify finished elevations;

- coordinate curbs/pavement;

- verify building thresholds;

- consider temporary drainage during construction.

12.4.3 DOCUMENT CONTROL

Verify:

☐ latest grading plan
☐ latest drain positions
☐ latest finished elevations
☐ pavement/curb interfaces current

12.4.4 MATERIAL CONTROL

Check:

- granular;

- surface materials;

- erosion-control materials;

- drainage stone;

- geotextile.

12.4.5 INSPECTION / TESTING

Check:

- surface slopes;

- swales;

- catch basin elevations;

- drainage away from building;

- transitions;

- localized depressions;

- erosion;

- blocked drains.

Where appropriate, observe water flow after rain or controlled testing.

12.4.6 RECORDS

Capture:

- survey grades;

- slope measurements;

- photos;

- ponding areas;

- corrective work.

12.4.7 NC / DEFICIENCY

Common:

- reverse slope;

- ponding;

- drain too high;

- surface slopes toward building;

- erosion;

- blocked inlet.

12.4.8 CORRECTIVE ACTION — EXAMPLE

Water ponds beside building after rainfall.

Document extent → compare grading plan → survey elevations → identify cause → regrade/adjust drain as authorized → verify drainage after correction → close.

12.4.9 VERIFICATION

Confirm positive drainage after correction.

12.4.10 CLOSURE

☐ final grades correct
☐ slopes correct
☐ drains operational
☐ no unintended ponding
☐ erosion controlled
☐ building perimeter drainage accepted

12.4.11 REPORTING / ANALYSIS

Track recurring ponding and grading deficiencies.

12.4.12 QUALITY CHECKPOINT

☐ Finished elevation
☐ Slopes
☐ Swales
☐ Catch basins
☐ Building perimeter
☐ Drainage flow
☐ Ponding
☐ Erosion
☐ Final verification

12.5 GRANULAR BASE / SUBBASE

This builds on our earlier granular module but focuses specifically on exterior pavement/site systems.

Quality objective

Construct pavement/base layers from approved granular materials at the required thickness, moisture, compaction, elevation and slope to provide a stable platform for final surfacing.

12.5.1 REQUIREMENTS

Obtain:

- pavement sections;

- civil details;

- granular specifications;

- approved source;

- geotechnical report;

- lift thickness;

- compaction requirement;

- testing frequency;

- final elevations;

- slopes;

- PIE/PRIE.

12.5.2 PLANNING

Establish:

- subgrade accepted;

- layer sequence;

- material deliveries;

- lift thickness;

- test frequency;

- final survey.

12.5.3 DOCUMENT CONTROL

Verify:

☐ correct pavement section
☐ correct granular type
☐ thickness
☐ compaction criterion
☐ final elevation/slope

12.5.4 MATERIAL CONTROL

Check:

- approved source;

- material type;

- contamination;

- moisture;

- segregation;

- delivery records where required.

12.5.5 INSPECTION / TESTING

Check:

- subgrade accepted;

- lift thickness;

- moisture;

- compaction;

- density tests;

- surface stability;

- elevation;

- slope.

12.5.6 RECORDS

Capture:

- area;

- layer;

- material;

- tests;

- failed/retest locations;

- elevations.

12.5.7 NC / DEFICIENCY

Common:

- wrong material;

- thick lift;

- failed density;

- wrong elevation;

- contamination;

- segregation;

- unstable base.

12.5.8 CORRECTIVE ACTION

Rework affected area → retest → re-survey.

12.5.9 VERIFICATION

Confirm compaction, thickness and elevation.

12.5.10 CLOSURE

☐ material approved
☐ layers complete
☐ compaction accepted
☐ elevation/slope correct
☐ testing complete
☐ ready for pavement

12.5.11 REPORTING / ANALYSIS

Track recurring density failures or supplier/material issues.

12.5.12 QUALITY CHECKPOINT

☐ Source
☐ Material
☐ Lift thickness
☐ Moisture
☐ Compaction
☐ Density tests
☐ Elevation
☐ Slope
☐ Surface condition

12.6 CURBS

Quality objective

Construct curbs in the correct line, elevation, profile and geometry with suitable concrete quality, joints and finish so they support drainage and pavement interfaces properly.

12.6.1 REQUIREMENTS

Obtain:

- civil plans;

- curb details;

- profiles;

- concrete specification;

- joint details;

- reinforcement if applicable;

- tolerances;

- curing requirements;

- PIE/PRIE.

12.6.2 PLANNING

Before curb work:

- survey line/elevation;

- base accepted;

- forms/layout ready;

- concrete/testing coordinated;

- drainage interfaces identified.

12.6.3 DOCUMENT CONTROL

Verify:

☐ curb type
☐ line
☐ elevation
☐ dimensions
☐ joint spacing
☐ current details

12.6.4 MATERIAL CONTROL

Check:

- concrete mix;

- reinforcement;

- forms;

- joint materials;

- curing materials.

12.6.5 INSPECTION / TESTING

Before pour

- base;

- line;

- elevation;

- dimensions;

- forms;

- reinforcement if any.

During pour

- concrete ticket;

- testing where required;

- placement;

- consolidation;

- finish.

After

- alignment;

- elevation;

- jointing;

- surface;

- curing;

- damage.

12.6.6 RECORDS

Capture:

- curb segment;

- survey;

- concrete/test info;

- alignment;

- defects.

12.6.7 NC / DEFICIENCY

Common:

- wrong elevation;

- poor alignment;

- damaged edge;

- inadequate finish;

- wrong joint location;

- drainage conflict.

12.6.8 CORRECTIVE ACTION — EXAMPLE

Curb section creates a low point preventing water from reaching catch basin.

Survey → compare profile → determine affected segment → correct/reconstruct as authorized → verify drainage → close.

12.6.9 VERIFICATION

Confirm line, elevation, profile and finish.

12.6.10 CLOSURE

☐ geometry correct
☐ concrete accepted
☐ joints complete
☐ curing complete
☐ drainage interface works
☐ defects closed

12.6.11 REPORTING / ANALYSIS

Track repeated alignment/elevation issues.

12.6.12 QUALITY CHECKPOINT

☐ Line
☐ Elevation
☐ Dimensions
☐ Base
☐ Concrete
☐ Joints
☐ Finish
☐ Curing
☐ Drainage interface

12.7 CONCRETE EXTERIOR WORKS

Examples:

- sidewalks;

- pads;

- aprons;

- ramps;

- exterior slabs;

- equipment pads;

- concrete channels.

Quality objective

Construct exterior concrete at the correct geometry, slope and finish using approved materials, with proper joints, curing and weather protection.

12.7.1 REQUIREMENTS

Obtain:

- civil/architectural plans;

- details;

- concrete specification;

- slope/elevation requirements;

- reinforcement;

- joint details;

- finish;

- curing;

- cold/hot weather requirements;

- accessibility requirements where applicable;

- PIE/PRIE.

12.7.2 PLANNING

Before pour:

- subgrade/base accepted;

- forms/layout;

- reinforcement;

- embeds;

- slope;

- concrete test coordination;

- weather;

- curing/protection.

12.7.3 DOCUMENT CONTROL

Verify:

☐ correct detail
☐ dimensions
☐ elevations
☐ slope
☐ reinforcement
☐ joints
☐ finish

12.7.4 MATERIAL CONTROL

Check:

- concrete mix;

- reinforcement;

- joint material;

- curing product;

- sealers where applicable.

12.7.5 INSPECTION / TESTING

Before:

- base;

- forms;

- reinforcement;

- slope;

- embeds.

During:

- delivery;

- testing;

- placement;

- consolidation;

- finishing.

After:

- slope;

- surface;

- joints;

- curing;

- cracking;

- edge damage.

12.7.6 RECORDS

Capture:

- pour ID;

- area;

- test results;

- slopes;

- joints;

- finish;

- defects.

12.7.7 NC / DEFICIENCY

Common:

- wrong slope;

- ponding;

- cracking;

- surface scaling;

- poor jointing;

- wrong finish;

- insufficient curing.

12.7.8 CORRECTIVE ACTION — EXAMPLE

Sidewalk section ponds water.

Survey/measure slope → identify extent → determine authorized correction → grind/reconstruct as permitted → verify drainage → document.

12.7.9 VERIFICATION

Confirm slope, surface and repaired condition.

12.7.10 CLOSURE

☐ dimensions correct
☐ slope correct
☐ concrete accepted
☐ joints complete
☐ finish accepted
☐ curing complete
☐ drainage works

12.7.11 REPORTING / ANALYSIS

Track recurring cracking, ponding or finish defects.

12.7.12 QUALITY CHECKPOINT

☐ Base
☐ Formwork
☐ Reinforcement
☐ Elevation
☐ Slope
☐ Concrete
☐ Finish
☐ Joints
☐ Curing
☐ Final drainage

12.8 ASPHALT

Quality objective

Place asphalt over an accepted base using approved mix and controlled placement/compaction so required thickness, density, grade, smoothness and drainage are achieved.

12.8.1 REQUIREMENTS

Obtain:

- pavement sections;

- asphalt specification;

- approved mix;

- layer thickness;

- tack/prime requirements;

- temperature requirements;

- compaction/density criteria;

- testing frequency;

- grades/slopes;

- joint requirements;

- PIE/PRIE.

12.8.2 PLANNING

Before paving:

- granular base accepted;

- elevations/slope checked;

- drainage structures adjusted;

- weather suitable;

- asphalt plant/mix confirmed;

- testing coordinated;

- paving sequence planned.

12.8.3 DOCUMENT CONTROL

Verify:

☐ correct mix
☐ layer thickness
☐ pavement limits
☐ grades
☐ testing requirement
☐ current details

12.8.4 MATERIAL CONTROL

Check:

- asphalt mix;

- delivery tickets;

- mix temperature;

- load identification;

- tack/prime materials.

12.8.5 INSPECTION / TESTING

Before placement

- base clean/dry;

- tack/prime applied where required;

- structures at correct level.

Placement

Check:

- temperature;

- thickness;

- segregation;

- paver operation;

- joints;

- edges.

Compaction

Check:

- rolling sequence;

- density;

- no displacement/rutting.

Final surface

Verify:

- smoothness;

- grade;

- drainage;

- joints;

- segregation;

- cracking;

- surface defects.

12.8.6 RECORDS

Capture:

- area;

- mix;

- tickets;

- temperatures;

- density tests;

- thickness;

- grades;

- photos.

12.8.7 NC / DEFICIENCY

Common:

- wrong mix;

- cold material;

- segregation;

- failed density;

- insufficient thickness;

- poor joint;

- ponding;

- rutting.

12.8.8 CORRECTIVE ACTION — EXAMPLE

Density testing fails localized asphalt area.

Identify exact area → compare criterion → determine authorized remediation → recompact if viable or remove/replace as directed → retest → document.

12.8.9 VERIFICATION

Confirm repaired area passes required checks.

12.8.10 CLOSURE

☐ approved mix
☐ thickness accepted
☐ density accepted
☐ joints accepted
☐ grade/drainage accepted
☐ surface accepted
☐ test records complete

12.8.11 REPORTING / ANALYSIS

Track:

- density failures;

- low temperatures;

- segregation;

- recurring ponding;

- supplier variability.

12.8.12 QUALITY CHECKPOINT

☐ Base accepted
☐ Mix approved
☐ Temperature
☐ Thickness
☐ Compaction
☐ Density
☐ Joints
☐ Grade
☐ Drainage
☐ Surface

12.9 SITE RESTORATION

Quality objective

Restore disturbed site areas to the required final condition without leaving unresolved damage, drainage problems, debris, temporary works or incomplete finishes.

12.9.1 REQUIREMENTS

Obtain:

- landscaping/site-restoration plans;

- grading plans;

- pavement details;

- topsoil/seed/sod requirements;

- demolition/restoration limits;

- owner/HQ requirements;

- environmental requirements;

- deficiency/turnover criteria.

12.9.2 PLANNING

Before restoration:

- temporary facilities removed;

- underground work complete;

- final grades established;

- drainage accepted;

- damaged existing features identified;

- final access requirements understood.

12.9.3 DOCUMENT CONTROL

Verify:

☐ restoration limits
☐ final grades
☐ finish materials
☐ existing-to-remain conditions
☐ current owner requirements

12.9.4 MATERIAL CONTROL

Check:

- topsoil;

- seed/sod;

- gravel;

- pavement materials;

- replacement curb;

- fencing;

- landscaping materials.

12.9.5 INSPECTION

Check:

- final grading;

- surface drainage;

- pavement repairs;

- curb/sidewalk restoration;

- landscaping;

- fencing;

- disturbed adjacent areas;

- removal of debris;

- temporary works removed;

- existing assets restored.

Compare final condition with baseline existing-condition records where relevant.

12.9.6 RECORDS

Capture:

- before/after photos;

- restored areas;

- final survey where required;

- deficiency list;

- owner observations.

12.9.7 NC / DEFICIENCY

Common:

- incomplete restoration;

- damaged pavement;

- ponding;

- debris;

- poor landscaping;

- damaged existing property;

- temporary materials left behind.

12.9.8 CORRECTIVE ACTION

Restore affected area to required condition → reinspect → document.

12.9.9 VERIFICATION

Compare:

baseline condition / project requirement → final restored condition

12.9.10 CLOSURE

☐ grades accepted
☐ drainage accepted
☐ surfaces restored
☐ landscape restored
☐ temporary works removed
☐ debris removed
☐ damage repaired
☐ final evidence complete

12.9.11 REPORTING / ANALYSIS

Track open restoration items blocking turnover.

12.9.12 QUALITY CHECKPOINT

☐ Restoration limits
☐ Grades
☐ Drainage
☐ Pavement
☐ Curbs/sidewalks
☐ Landscape
☐ Existing assets
☐ Cleanup
☐ Final photos

12.10 FENCING / GATES — IF APPLICABLE

For a substation project, this could be especially important because perimeter control and secure access may be significant project requirements.

Quality objective

Install fencing and gates at the correct alignment and elevation, with approved materials, stable foundations, complete hardware and required operational/security performance.

12.10.1 REQUIREMENTS

Obtain:

- site plan;

- fencing layout;

- fence/gate specifications;

- approved shop drawings;

- post/foundation details;

- gate schedule;

- hardware;

- grounding/bonding requirements where applicable;

- security/access-control interfaces;

- coatings;

- PIE/PRIE.

12.10.2 PLANNING

Before installation:

- survey alignment;

- identify gate locations;

- identify underground utilities;

- verify post foundations;

- coordinate security/electrical interfaces;

- verify grading along fence line.

12.10.3 DOCUMENT CONTROL

Verify:

☐ fence type
☐ height
☐ alignment
☐ gate type/width
☐ post details
☐ security interface
☐ latest revisions

12.10.4 MATERIAL CONTROL

Check:

- posts;

- rails;

- mesh/panels;

- fasteners;

- gates;

- hinges;

- locks;

- hardware;

- coatings/galvanizing;

- foundations;

- security devices.

12.10.5 INSPECTION / TESTING

Fence line

Check:

- alignment;

- height;

- plumb posts;

- spacing;

- tension;

- clearances;

- bottom gaps where controlled.

Foundations

Check:

- location;

- dimensions;

- concrete;

- stability.

Gates

Check:

- width;

- alignment;

- swing/slide;

- clearances;

- stops;

- hinges/rollers;

- locking hardware.

Security/access

Where applicable:

- access-control device physical installation;

- sensor/interface;

- grounding/bonding physical interface.

🟠 Specialized electrical/security functional testing remains with appropriate specialists.

12.10.6 RECORDS

Capture:

- fence segment;

- gate ID;

- alignment;

- foundations;

- hardware;

- coatings;

- functional test reference.

12.10.7 NC / DEFICIENCY

Common:

- posts out of plumb;

- poor alignment;

- loose fence;

- gate binds;

- incorrect gate clearance;

- damaged galvanizing;

- missing hardware;

- security interface incomplete.

12.10.8 CORRECTIVE ACTION — EXAMPLE

Vehicle gate closes but cannot latch because posts are misaligned.

Measure → adjust/reconstruct affected post/gate hardware → retest full operation → verify locking/security interface → document closure.

12.10.9 VERIFICATION

Physically operate gate and inspect final fence alignment.

12.10.10 CLOSURE

☐ fence alignment accepted
☐ posts stable
☐ mesh/panels complete
☐ coatings accepted
☐ gate operates
☐ hardware complete
☐ security interfaces complete
☐ specialist testing available where required

12.10.11 REPORTING / ANALYSIS

Track:

- recurring post alignment;

- coating damage;

- gate operation defects;

- security-interface issues.

12.10.12 QUALITY CHECKPOINT

☐ Layout
☐ Fence type
☐ Height
☐ Posts
☐ Foundations
☐ Alignment
☐ Panels/mesh
☐ Coating
☐ Gate
☐ Hardware
☐ Operation
☐ Security interface

EXTERNAL WORKS — MASTER PRE-CONCEALMENT GATE

Before any underground work is buried:

DOCUMENTS

☐ Latest civil/utility drawings
☐ Profiles
☐ Approved materials
☐ Technical changes
☐ Applicable PIE/PRIE

EXCAVATION

☐ Correct route
☐ Correct bottom elevation
☐ Suitable trench/subgrade condition

SERVICE

☐ Correct service
☐ Correct material/size
☐ Correct elevation/slope
☐ Joints complete
☐ Crossings/separations complete

STRUCTURES

☐ Manholes/catch basins accepted
☐ Inverts correct
☐ Connections complete

TESTING

☐ Required tests complete
☐ Failures repaired/retested

TRACEABILITY

☐ As-built survey captured
☐ Photos complete
☐ Service ID recorded

BEFORE BACKFILL

☐ Inspection complete
☐ Required release obtained
☐ No unresolved deficiency being buried

EXTERNAL WORKS — FINAL SITE QUALITY GATE

Before external works are considered complete:

BELOW GRADE

☐ Utilities accepted
☐ Testing complete
☐ As-builts complete
☐ Structures complete

EARTHWORKS

☐ Backfill complete
☐ Compaction accepted
☐ Base/subbase accepted

DRAINAGE

☐ Finished grades correct
☐ Catch basins/drains functional
☐ No unintended ponding

SURFACES

☐ Curbs complete
☐ Concrete works complete
☐ Asphalt complete
☐ Joints/transitions accepted

SITE

☐ Restoration complete
☐ Fencing/gates complete where applicable
☐ Existing assets restored
☐ Temporary works removed
☐ Final cleanup complete

DOCUMENTATION

☐ Survey/as-builts
☐ Test results
☐ Material approvals
☐ Inspection records
☐ Photographs
☐ NCR/deficiency closure
☐ Responsable qualité updated

PRACTICAL EXAMPLE — UNDERGROUND ELECTRICAL DUCT BANK

This is particularly relevant to the environment you're entering.

Suppose electrical duct bank is being installed tomorrow.

You should cross-reference:

External Works → Underground Services
External Works → Utility Trenches
Electrical → Conduits/Raceways
Structural ↔ Electrical
and, where concrete encased,
Concrete workflow

Your sequence:

1. Before installation

Check:

- latest duct-bank layout;

- conduit type/size;

- number of conduits;

- route;

- elevations;

- trench/bedding;

- spacers;

- structural/concrete details;

- pull-box/equipment endpoints.

2. Installation

Check:

- conduit configuration;

- spacing;

- alignment;

- joints;

- support/spacers;

- bends;

- termination/stub-ups.

3. Before encasement/backfill

This is the key gate:

- conduit route confirmed;

- dimensions;

- elevations;

- test/mandrel requirement;

- photos;

- survey;

- reinforcement if any;

- no damaged conduit.

4. Concrete encasement where required

Use concrete controls.

5. After

- verify no displacement;

- as-built complete;

- subsequent backfill/compaction controlled.

Now you have not inspected merely “some pipes in a trench.” You have controlled the entire civil-electrical interface.

BUILD 2 — EXTERNAL WORKS STATUS

12.1 Underground Services ✓
12.2 Utility Trenches ✓
12.3 Manholes/Catch Basins/Structures ✓
12.4 Exterior Drainage ✓
12.5 Granular Base/Subbase ✓
12.6 Curbs ✓
12.7 Concrete Exterior Works ✓
12.8 Asphalt ✓
12.9 Site Restoration ✓
12.10 Fencing/Gates ✓

Absolutely. This is the point where the whole field-quality system starts proving whether the installed work actually performs.

The governing principle for this section is:

Inspection confirms that work appears and is documented as compliant. Testing and commissioning confirm that systems actually perform as required.

Your role is to make sure testing is properly planned, traceable, complete, witnessed/documented as required, failures are controlled, corrective actions are verified, retesting occurs, and the final acceptance evidence is complete.

Where technical acceptance belongs to a mechanical, electrical, controls, fire-protection, envelope, manufacturer, commissioning, or professional specialist:

🟠 VERIFY THE APPLICABLE PIE/PRIE / PROCEDURE → COORDINATE THE AUTHORIZED SPECIALIST → RETAIN THE ACCEPTANCE EVIDENCE.

13. TESTING, COMMISSIONING & SYSTEM ACCEPTANCE

Overall quality objective

Demonstrate, through controlled and traceable testing and commissioning, that completed systems and equipment satisfy the project requirements, function as intended, and are supported by complete acceptance documentation before turnover.

The universal workflow is:

Construction complete → readiness confirmed → approved test procedure → instruments/personnel ready → test performed → result recorded → failure controlled if any → corrective action → retest → specialist acceptance → system closure

13.1 TEST READINESS

Quality objective

Confirm that a system is genuinely ready to be tested before testing begins, so results are meaningful and test failures are not caused by incomplete construction or poor preparation.

This is one of the most important commissioning controls because premature testing wastes time and can produce misleading results.

13.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- testing and commissioning plan;

- Plan Qualité;

- applicable PIE/PRIE;

- approved test procedures;

- system drawings;

- equipment shop drawings;

- manufacturer start-up instructions;

- mechanical/electrical testing specifications;

- controls sequences;

- balancing requirements;

- envelope test procedures;

- fire/life-safety interface requirements;

- deficiency status;

- prerequisite test requirements;

- commissioning schedule;

- technical directives;

- QMT/RFI responses.

For each test, extract:

- system/equipment being tested;

- test boundary;

- prerequisites;

- test method;

- required instruments;

- calibration;

- witnesses;

- acceptance authority;

- acceptance criteria;

- documentation required.

13.1.2 PLANNING

Create a Test Readiness Checklist for every major test.

Before scheduling, ask:

Physical completion

- Is installation complete?

- Are all required components installed?

- Are temporary components removed or identified?

- Are supports/anchors complete?

- Are penetrations complete?

- Is insulation complete where required before test?

- Are labels/tags present?

Construction quality

- Are open deficiencies affecting the test resolved?

- Have prerequisite inspections passed?

- Have previous test failures been closed?

Utilities

- Is electrical power available where required?

- Water?

- Controls?

- drainage?

- compressed air?

- network/BAS?

Safety

- Is the system safe to energize/pressurize/start?

- Are isolation points identified?

- Are required safety approvals complete?

Documentation

- Current approved procedure?

- Current drawings?

- Equipment tag correct?

- Test form ready?

Personnel

- Qualified testing specialist available?

- Manufacturer representative required?

- Consultant/owner witness required?

- Responsable qualité notified?

Instruments

- Correct instrument?

- Calibration valid?

- Range appropriate?

13.1.3 DOCUMENT CONTROL

Verify:

☐ correct test procedure revision
☐ latest system drawing
☐ latest equipment submittal
☐ current sequence of operation
☐ current deficiency status
☐ current test form
☐ witness requirements known

13.1.4 MATERIAL / EQUIPMENT CONTROL

Verify availability and condition of:

- test gauges;

- meters;

- sensors;

- pumps;

- hoses;

- temporary connections;

- load banks where applicable;

- balancing instruments;

- manufacturer test equipment;

- calibrated electrical test equipment;

- leak-detection equipment;

- envelope test apparatus.

13.1.5 INSPECTION / READINESS REVIEW

Perform a physical walkdown.

Do not approve readiness from paperwork alone.

Verify:

drawing → physical system → equipment tag → connections → access → test boundary

The system should be complete enough that the test evaluates performance, not unfinished construction.

13.1.6 RECORDS / EVIDENCE

Capture:

- system/equipment ID;

- readiness checklist;

- date;

- open prerequisites;

- person responsible;

- readiness status;

- photos where useful;

- required releases.

Suggested statuses:

NOT READY → READY WITH HOLD ITEMS → READY FOR TEST → TESTED

Use CRT terminology once known.

13.1.7 NC / DEFICIENCY

Typical readiness failures:

- missing component;

- incomplete wiring;

- valve in wrong state;

- untested piping section;

- missing firestop;

- control point incomplete;

- equipment unanchored;

- calibration expired;

- manufacturer prerequisite missing.

13.1.8 CORRECTIVE ACTION — EXAMPLE

AHU start-up scheduled, but condensate drain is incomplete and controls are not connected.

Correct response:

Do not conduct meaningless start-up just because contractor is mobilized.

Record readiness failure → identify missing prerequisites → assign → complete → re-walk system → release start-up only when appropriate.

13.1.9 VERIFICATION

Recheck every previously open readiness item.

13.1.10 CLOSURE

Test readiness closes when:

☐ installation complete enough
☐ prerequisites passed
☐ test procedure current
☐ instruments ready
☐ qualified personnel scheduled
☐ witnesses notified
☐ open defects controlled
☐ system safe/available for test
☐ readiness evidence complete

13.1.11 REPORTING / ANALYSIS

Track:

- tests delayed by construction;

- repeated readiness failures;

- missing documentation;

- late controls;

- late utilities;

- recurring manufacturer issues.

This helps identify why commissioning is slipping.

13.1.12 QUALITY CHECKPOINT

☐ Physical completion
☐ Prerequisite inspections
☐ Utilities available
☐ Open defects reviewed
☐ Approved procedure
☐ Test form
☐ Instruments/calibration
☐ Qualified personnel
☐ Witnesses
☐ Safety readiness
☐ System released

13.2 TEST DOCUMENTATION

Quality objective

Ensure every test is supported by complete, legible, traceable and technically attributable documentation showing what was tested, how, by whom, with what equipment, against what criterion, and with what result.

A test without traceable documentation is weak evidence.

13.2.1 REQUIREMENTS

Obtain:

- project test forms;

- PIE/PRIE record requirements;

- commissioning forms;

- instrument calibration requirements;

- signature requirements;

- witness requirements;

- electronic filing rules;

- document naming conventions.

13.2.2 PLANNING

Before test, prepare the record so nobody is trying to reconstruct details afterward.

Fields should include:

- project;

- system;

- equipment tag;

- location;

- test package;

- drawing;

- procedure;

- date;

- time;

- tester;

- company;

- witness;

- instrument;

- calibration;

- environmental conditions where relevant;

- criterion;

- actual result;

- pass/fail;

- observations;

- defect;

- corrective action;

- retest;

- signatures.

13.2.3 DOCUMENT CONTROL

Verify:

☐ correct form revision
☐ correct equipment/system ID
☐ current procedure referenced
☐ current criteria
☐ document number assigned where required

13.2.4 MATERIAL / EQUIPMENT CONTROL

Documentation should capture the actual instruments used.

For example:

Pressure gauge PG-12 → Calibration certificate CAL-021 → valid through date X

where required.

13.2.5 INSPECTION / TESTING

During test:

- fill record contemporaneously;

- record actual readings;

- do not backfill data from memory later;

- identify anomalies;

- identify interruptions;

- identify retests separately.

13.2.6 RECORDS / EVIDENCE

The test form itself is the primary output, supported by:

- photos;

- graphs;

- screenshots;

- instrument printouts;

- manufacturer reports;

- data logs;

- calibration certificate;

- witness signatures.

13.2.7 NC / DEFICIENCY

Documentation issues include:

- missing equipment ID;

- missing criterion;

- unsigned test;

- incorrect date;

- unclear result;

- no calibration evidence;

- overwritten failed result;

- retest replacing original failed report.

Critical rule

Never erase the history of a failure.

The audit trail should show:

initial failure → corrective action → retest → acceptance

13.2.8 CORRECTIVE ACTION

Complete missing information only with valid traceable evidence.

Do not invent data retrospectively.

If a required test cannot be substantiated:

🟠 determine whether the test must be repeated.

13.2.9 VERIFICATION

Review test package for:

- completeness;

- traceability;

- signatures;

- criteria;

- result;

- calibration;

- failure history.

13.2.10 CLOSURE

☐ test report complete
☐ all attachments present
☐ result unambiguous
☐ acceptance authority documented
☐ failures/retests traceable
☐ filed correctly

13.2.11 REPORTING / ANALYSIS

Track missing/incomplete test records because paperwork backlog can become a turnover risk even when physical construction is complete.

13.2.12 QUALITY CHECKPOINT

☐ System ID
☐ Equipment ID
☐ Procedure
☐ Criterion
☐ Tester
☐ Witness
☐ Instrument
☐ Calibration
☐ Readings
☐ Result
☐ Defect/correction
☐ Retest
☐ Signatures
☐ Attachments
☐ Filing

13.3 MECHANICAL TESTING

This consolidates the testing interfaces from our Mechanical module.

Quality objective

Demonstrate that installed mechanical systems are leak-free, clean, operational and capable of meeting specified functional requirements through controlled testing and specialist acceptance.

13.3.1 REQUIREMENTS

Obtain:

- mechanical test specifications;

- approved test procedures;

- pressure test criteria;

- leak test criteria;

- flushing/cleaning requirements;

- TAB requirements;

- equipment start-up requirements;

- controls sequences;

- commissioning forms;

- PIE/PRIE.

13.3.2 PLANNING

Break mechanical testing into packages:

- domestic water;

- drainage;

- piping;

- ductwork;

- equipment;

- controls;

- balancing.

Identify test sequence.

Example:

piping installed → pressure test → repair/retest → flush → insulate → start equipment → control verification → balancing → functional test

13.3.3 DOCUMENT CONTROL

Verify:

☐ correct system boundary
☐ current test procedure
☐ current schematic
☐ acceptance criteria
☐ current commissioning form

13.3.4 MATERIAL / EQUIPMENT CONTROL

Verify:

- calibrated gauges;

- pumps;

- temporary connections;

- flow instruments;

- balancing instruments;

- manufacturer tools.

13.3.5 INSPECTION / TESTING

Potential testing:

Piping

- pressure;

- leak;

- flushing;

- cleaning.

Ductwork

- leakage;

- pressure;

- visual seal inspection.

Equipment

- rotation where applicable;

- operating condition;

- vibration;

- startup checks.

Controls

- sensor/actuator response;

- equipment command;

- control sequence interface.

TAB

Review specialist balancing report.

🟠 Specialized performance acceptance remains with authorized mechanical/commissioning personnel.

13.3.6 RECORDS / EVIDENCE

Capture:

- test package;

- system;

- instrument;

- results;

- failed locations;

- repair;

- retest;

- TAB reports;

- start-up sheets;

- commissioning sign-off.

13.3.7 NC / DEFICIENCY

Typical:

- pressure drop;

- leak;

- dirty system;

- inaccessible balancing device;

- equipment abnormal vibration;

- controls mismatch;

- balancing outside target.

13.3.8 CORRECTIVE ACTION — EXAMPLE

Duct leakage test fails.

Identify test zone → locate leakage points → repair seams/joints → repeat complete required test → document both initial fail and final pass.

13.3.9 VERIFICATION

Confirm repair and successful retest.

13.3.10 CLOSURE

☐ required mechanical tests complete
☐ failures corrected
☐ retests passed
☐ flushing/cleaning complete
☐ equipment start-up complete
☐ TAB complete where required
☐ specialist acceptance complete
☐ records filed

13.3.11 REPORTING / ANALYSIS

Track:

- mechanical test pass rate;

- repeated leak types;

- balancing failures;

- commissioning blockers;

- equipment issues.

13.3.12 QUALITY CHECKPOINT

☐ Test package
☐ Procedure
☐ Instrument
☐ Pressure/leak test
☐ Flush/clean
☐ Equipment start-up
☐ Controls
☐ TAB
☐ Corrective action
☐ Retest
☐ Specialist acceptance

13.4 ELECTRICAL TESTING INTERFACES

We keep the technical-authority boundary firm.

Quality objective

Ensure required electrical tests are planned, traceable and documented, with technical acceptance provided by authorized electrical specialists and all failures fully closed before energization/turnover.

13.4.1 REQUIREMENTS

Obtain:

- electrical test specifications;

- PIE/PRIE;

- approved test procedures;

- equipment manufacturer instructions;

- cable test requirements;

- grounding test requirements;

- functional test requirements;

- commissioning plan;

- energization prerequisites.

13.4.2 PLANNING

For every equipment/system:

- identify required test;

- identify test specialist;

- verify system ready;

- identify witness;

- verify instrument calibration;

- identify energization dependency.

13.4.3 DOCUMENT CONTROL

Verify:

☐ current test procedure
☐ correct equipment tag
☐ current one-line/drawing
☐ test form
☐ specialist acceptance requirement

13.4.4 MATERIAL / EQUIPMENT CONTROL

Check evidence for calibrated specialist test instruments.

13.4.5 TESTING INTERFACE

Your process-control questions:

- Is the correct equipment being tested?

- Is the approved test being used?

- Are required witnesses present?

- Is the result documented?

- Is the specialist acceptance clear?

- Did a failed test trigger corrective action and retest?

Potential tests may include:

- continuity;

- insulation resistance;

- grounding;

- cable testing;

- functional tests;

- emergency lighting;

- equipment controls;

- protection/control systems;

- specialized substation tests.

🟠 Exact technical criteria come from authorized electrical procedures/personnel.

13.4.6 RECORDS

Capture:

- equipment tag;

- test reference;

- specialist;

- instrument;

- result;

- deficiency;

- retest;

- acceptance.

13.4.7 NC / DEFICIENCY

Typical:

- missing test;

- wrong equipment ID;

- failed test;

- no specialist acceptance;

- missing calibration;

- test performed before completion;

- energization attempted before closure.

13.4.8 CORRECTIVE ACTION

Failure → control status → electrical specialist diagnoses → corrective work → retest → specialist acceptance.

13.4.9 VERIFICATION

Verify process completion, not technical reinterpretation.

13.4.10 CLOSURE

☐ required tests complete
☐ failures closed
☐ specialist acceptance recorded
☐ energization prerequisite cleared
☐ test records filed

13.4.11 REPORTING / ANALYSIS

Track:

- electrical test status;

- open fails;

- retests;

- commissioning/energization blockers.

13.4.12 QUALITY CHECKPOINT

☐ System/equipment
☐ Required test
☐ Procedure
☐ Specialist
☐ Instrument/calibration
☐ Result
☐ Failure status
☐ Retest
☐ Acceptance
☐ Energization dependency

13.5 BUILDING ENVELOPE TESTING

Quality objective

Demonstrate that the completed building envelope achieves required water, air and membrane-integrity performance at the tested assemblies and interfaces.

13.5.1 REQUIREMENTS

Obtain:

- envelope test specification;

- window test requirements;

- roof test requirements;

- air leakage requirements;

- water penetration test;

- electronic leak detection requirements;

- mock-up procedures;

- manufacturer requirements;

- PIE/PRIE.

13.5.2 PLANNING

Before test:

- assembly substantially complete;

- test zone defined;

- penetrations/flashings complete;

- interior accessible for leak observation;

- test equipment ready;

- specialists/witnesses coordinated.

13.5.3 DOCUMENT CONTROL

Verify:

☐ approved test method
☐ test location
☐ acceptance criteria
☐ current envelope details
☐ current test report template

13.5.4 MATERIAL / EQUIPMENT CONTROL

Examples:

- spray rack;

- pressure equipment;

- air leakage apparatus;

- electronic membrane testing equipment;

- calibrated gauges.

13.5.5 INSPECTION / TESTING

Possible tests:

Windows / wall openings

- water penetration;

- air leakage.

Roof

- electronic leak detection;

- controlled water test if specified.

Envelope

- whole-building/zone air leakage if specified.

Mock-ups

- performance verification before repetitive work.

Observe:

- exact leak location;

- pressure/conditions;

- test duration;

- failure pathway;

- test zone.

13.5.6 RECORDS

Capture:

- test zone;

- assembly;

- procedure;

- pressure/conditions;

- photos/video where appropriate;

- result;

- leak location;

- repair;

- retest.

13.5.7 NC / DEFICIENCY

Typical:

- water infiltration;

- excessive air leakage;

- membrane breach;

- flashing failure;

- sealant failure;

- failed window interface.

13.5.8 CORRECTIVE ACTION — EXAMPLE

Window water test fails at sill corner.

Do not simply add sealant indiscriminately.

Identify actual water path → inspect sill/jamb/flashing interface → apply approved corrective method → repeat same test → document passing retest.

13.5.9 VERIFICATION

Retest the corrected assembly using required method.

13.5.10 CLOSURE

☐ required envelope tests complete
☐ failures repaired
☐ retests passed
☐ test evidence complete
☐ specialist/manufacturer acceptance complete where required

13.5.11 REPORTING / ANALYSIS

Track:

- leak locations;

- recurring details;

- installer-specific issues;

- repeated failures at same interface type.

13.5.12 QUALITY CHECKPOINT

☐ Test zone
☐ Assembly complete
☐ Procedure
☐ Equipment
☐ Conditions
☐ Result
☐ Failure location
☐ Repair
☐ Retest
☐ Acceptance

13.6 FUNCTIONAL TESTING

Quality objective

Verify that installed equipment and systems actually perform their intended operational functions, not merely that they have been installed.

Examples:

- door closes and latches;

- valve operates;

- damper opens/closes;

- HVAC responds to command;

- drain actually drains;

- emergency light operates;

- alarm interface triggers expected physical response.

13.6.1 REQUIREMENTS

Obtain:

- sequence of operation;

- functional performance test scripts;

- controls diagrams;

- manufacturer requirements;

- commissioning plan;

- life-safety interface matrix;

- PIE/PRIE.

13.6.2 PLANNING

For each function:

Input → expected response → actual response → acceptance

Example:

BAS calls for fan ON → fan starts → status feedback confirms → airflow condition achieved.

Your role may be to witness/document rather than technically commission.

13.6.3 DOCUMENT CONTROL

Verify:

☐ current sequence
☐ current test script
☐ correct equipment tags
☐ current controls configuration
☐ acceptance authority

13.6.4 MATERIAL / EQUIPMENT CONTROL

Ensure relevant equipment/devices are installed and ready.

13.6.5 FUNCTIONAL TESTING

Check, depending on scope:

- equipment starts/stops;

- valves move;

- dampers respond;

- doors release/close;

- lighting switches;

- emergency functions operate;

- alarms/signals produce expected response;

- interlocks operate.

🟠 Complex logic should be accepted by controls/fire/electrical/mechanical commissioning specialists.

13.6.6 RECORDS

Capture:

- function tested;

- initiating condition;

- expected response;

- actual response;

- result;

- deficiency;

- retest.

13.6.7 NC / DEFICIENCY

Examples:

- fan doesn't start;

- damper moves opposite command;

- door release fails;

- valve actuator doesn't fully stroke;

- alarm input doesn't trigger expected interface.

13.6.8 CORRECTIVE ACTION

Identify responsible system/trade → correct → repeat full affected function.

13.6.9 VERIFICATION

Verify end-to-end function, not just replaced component.

13.6.10 CLOSURE

☐ function performed
☐ expected response achieved
☐ deficiencies closed
☐ retest passed
☐ specialist acceptance documented

13.6.11 REPORTING / ANALYSIS

Track functional failures by:

- system;

- interface;

- root cause;

- responsible discipline.

13.6.12 QUALITY CHECKPOINT

☐ Function identified
☐ Expected response
☐ Test script
☐ Required specialists
☐ Actual response
☐ Result
☐ Correction
☐ Retest
☐ Acceptance

13.7 EQUIPMENT START-UP

Quality objective

Ensure equipment is initially started under controlled conditions, in accordance with manufacturer/project procedures, with installation prerequisites complete and start-up data properly recorded.

13.7.1 REQUIREMENTS

Obtain:

- manufacturer start-up procedure;

- equipment manual;

- commissioning plan;

- equipment submittal;

- installation checklist;

- electrical/mechanical prerequisites;

- controls requirements;

- lubrication/fluids;

- PIE/PRIE.

13.7.2 PLANNING

Before start-up:

- equipment anchored;

- shipping restraints removed where applicable;

- connections complete;

- filters installed;

- lubrication complete;

- valves correct;

- electrical acceptance complete;

- controls available;

- drains connected;

- guards installed;

- manufacturer rep available if required.

13.7.3 DOCUMENT CONTROL

Verify:

☐ correct equipment
☐ current manufacturer procedure
☐ current approved configuration
☐ start-up form
☐ prerequisite tests complete

13.7.4 MATERIAL / EQUIPMENT CONTROL

Check:

- consumables;

- filters;

- belts;

- lubricants;

- accessories;

- spare components if needed.

13.7.5 START-UP

Observe/document where assigned:

- initial energization;

- abnormal noise;

- vibration;

- leakage;

- rotation;

- temperature;

- pressure;

- alarms;

- controls status.

Again, technical acceptance belongs to appropriate specialist.

13.7.6 RECORDS

Capture:

- equipment tag;

- model/serial;

- date;

- start-up technician;

- manufacturer rep;

- readings;

- observations;

- deficiencies;

- approval.

13.7.7 NC / DEFICIENCY

Typical:

- equipment will not start;

- excessive vibration;

- leak;

- wrong rotation;

- alarm;

- missing controls;

- missing manufacturer prerequisite.

13.7.8 CORRECTIVE ACTION — EXAMPLE

Pump starts but exhibits abnormal vibration.

Do not simply leave it running.

Stop/control per responsible specialist → document → inspect alignment/support/installation → specialist diagnosis → correction → repeat start-up → retain passing record.

13.7.9 VERIFICATION

Repeat start-up/function after correction.

13.7.10 CLOSURE

☐ prerequisites complete
☐ start-up performed
☐ equipment stable
☐ no unresolved alarm/leak/vibration
☐ manufacturer/start-up record complete
☐ ready for functional testing

13.7.11 REPORTING / ANALYSIS

Track startup failures, shipping damage, installation-related startup issues.

13.7.12 QUALITY CHECKPOINT

☐ Equipment tag
☐ Installation complete
☐ Electrical/mechanical ready
☐ Manufacturer procedure
☐ Start-up technician
☐ Initial operation
☐ Abnormal conditions
☐ Corrections
☐ Restart/retest
☐ Record

13.8 INTEGRATED / SYSTEM TESTING — WHERE APPLICABLE

This is where separate systems are tested together.

Quality objective

Verify that interacting systems operate correctly as an integrated facility under defined scenarios.

Examples:

- fire alarm → damper → door release → emergency system;

- emergency power → emergency lighting;

- BAS → HVAC equipment;

- equipment shutdown/interlock sequences.

13.8.1 REQUIREMENTS

Obtain:

- integrated testing plan;

- cause/effect matrix;

- sequences;

- fire/life-safety interface matrix;

- controls diagrams;

- commissioning scripts;

- PIE/PRIE;

- specialist responsibilities.

13.8.2 PLANNING

Before integrated testing:

- every individual system must be substantially tested first;

- system specialists available;

- scenario defined;

- safety reviewed;

- test script approved;

- witnesses identified;

- reset procedure known.

Critical rule

Do not use integrated testing to discover that basic individual systems were never completed.

13.8.3 DOCUMENT CONTROL

Verify:

☐ current cause/effect matrix
☐ test script
☐ current sequences
☐ equipment IDs
☐ current deficiencies
☐ acceptance authority

13.8.4 MATERIAL / EQUIPMENT CONTROL

Ensure relevant systems and test tools available.

13.8.5 TESTING

For each scenario:

Initiating event

What starts the sequence?

Expected chain

What systems should respond?

Actual chain

What happened?

Timing

Where applicable, was sequence correct?

Reset

Does system return to correct state?

13.8.6 RECORDS

Capture:

- scenario ID;

- initiating event;

- systems involved;

- expected responses;

- actual responses;

- failures;

- corrective actions;

- retest;

- specialist sign-off.

13.8.7 NC / DEFICIENCY

Common:

- one interface fails;

- incorrect sequence;

- missing signal;

- system fails to reset;

- device operates opposite expected logic.

13.8.8 CORRECTIVE ACTION — EXAMPLE

Fire alarm signal correctly activates but associated damper does not close.

Record interface failure → determine whether mechanical actuator, fire-alarm signal, controls, or wiring is responsible → correct responsible component/system → repeat full scenario → verify all related responses → close.

13.8.9 VERIFICATION

Retest the integrated sequence, not merely the failed component.

13.8.10 CLOSURE

☐ individual systems tested
☐ integrated scenarios completed
☐ interfaces correct
☐ failures resolved
☐ full retest passed
☐ authorized acceptance documented

13.8.11 REPORTING / ANALYSIS

Track interface failures separately because they expose coordination weaknesses.

13.8.12 QUALITY CHECKPOINT

☐ Scenario
☐ Initiating event
☐ Expected response
☐ Systems involved
☐ Specialists present
☐ Actual response
☐ Failures
☐ Correction
☐ Full retest
☐ Acceptance

13.9 FAILED-TEST MANAGEMENT

This deserves its own workflow because failures must never disappear inside paperwork.

Quality objective

Ensure every failed test is immediately identifiable, controlled, investigated, corrected, retested and traceably closed without losing the original failure record.

13.9.1 REQUIREMENTS

Obtain:

- NCR/deficiency procedure;

- failed-test procedure;

- test acceptance authority;

- corrective-action process;

- escalation matrix;

- retest requirements;

- PIE/PRIE.

13.9.2 PLANNING

Set up a Failed-Test Register.

Suggested fields:

| ID | System | Test | Failure | Date | Action | Retest | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |

13.9.3 DOCUMENT CONTROL

Maintain:

- original failed report;

- correction record;

- retest report;

- approval.

Never replace original failed test with later passing test.

13.9.4 MATERIAL / EQUIPMENT CONTROL

If failure involves defective component/material, control the affected item.

13.9.5 FAILED-TEST PROCESS

Step 1 — Identify

What failed?

Step 2 — Control

Prevent premature acceptance/use/energization.

Step 3 — Document

Record exact result.

Step 4 — Notify

Responsible trade + Responsable qualité + specialist.

Step 5 — Diagnose

Authorized technical personnel determine cause.

Step 6 — Correct

Implement approved correction.

Step 7 — Reinspect

Verify physical correction.

Step 8 — Retest

Repeat required test.

Step 9 — Accept

Authorized specialist accepts.

Step 10 — Close

Update register and quality status.

13.9.6 RECORDS

Keep:

FAIL → CORRECTION → RETEST → PASS → ACCEPTANCE

as one traceable chain.

13.9.7 NC / DEFICIENCY

A failed test may itself trigger:

- deficiency;

- NCR;

- corrective-action report;

depending on CRT procedure and significance.

13.9.8 CORRECTIVE ACTION

Actual corrective action depends on specialist diagnosis.

Your control responsibility is making sure it is authorized, performed, verified and retested.

13.9.9 VERIFICATION

Verify:

- correction completed;

- affected system restored;

- retest required;

- retest passed.

13.9.10 CLOSURE

☐ original failure retained
☐ root cause/disposition documented where required
☐ corrective action complete
☐ retest passed
☐ specialist accepted
☐ register updated
☐ dependent activities released

13.9.11 REPORTING / ANALYSIS

This becomes a useful management dashboard:

- total failed tests;

- open fails;

- aging;

- system;

- subcontractor;

- failure type;

- recurrence;

- commissioning impact.

13.9.12 QUALITY CHECKPOINT

☐ Failure ID
☐ Test report
☐ System controlled
☐ Notification
☐ Diagnosis
☐ Correction
☐ Reinspection
☐ Retest
☐ Pass
☐ Acceptance
☐ Register updated

13.10 RETESTING

Quality objective

Confirm that corrective work actually resolves the failed condition by repeating the required test under valid conditions and maintaining traceability to the original failure.

13.10.1 REQUIREMENTS

Obtain:

- original test procedure;

- required retest scope;

- specialist instructions;

- PIE/PRIE;

- revised technical disposition if applicable.

13.10.2 PLANNING

Before retest:

- correction complete;

- system restored;

- test boundary confirmed;

- original failure reviewed;

- instruments ready;

- witnesses scheduled.

13.10.3 DOCUMENT CONTROL

Verify:

☐ original failed test reference
☐ corrective-action reference
☐ current procedure
☐ retest form

13.10.4 MATERIAL / EQUIPMENT CONTROL

Same instrument/calibration requirements apply.

13.10.5 RETEST

Repeat test to required scope.

Do not weaken acceptance criteria simply because this is a retest.

13.10.6 RECORDS

Link:

Retest report → original failure → corrective action

13.10.7 NC / DEFICIENCY

If retest fails again:

- item remains open;

- escalate recurring failure;

- reassess correction/root cause;

- do not cycle repairs indefinitely without analysis.

13.10.8 CORRECTIVE ACTION

Further authorized technical investigation.

13.10.9 VERIFICATION

Confirm passing retest and specialist acceptance.

13.10.10 CLOSURE

☐ correction completed
☐ original failure referenced
☐ valid retest performed
☐ pass obtained
☐ acceptance documented
☐ all records linked

13.10.11 REPORTING / ANALYSIS

Repeated retests are a strong signal for root-cause/trend review.

13.10.12 QUALITY CHECKPOINT

☐ Original fail
☐ Corrective action
☐ Procedure
☐ Instruments
☐ Retest
☐ Result
☐ Specialist acceptance
☐ Traceability
☐ Closure

13.11 ACCEPTANCE EVIDENCE

This is the final output of the entire testing/commissioning system.

Quality objective

Compile a complete, traceable body of evidence demonstrating that each system has been inspected, tested, corrected where necessary, accepted by the appropriate authority and is ready for turnover.

13.11.1 REQUIREMENTS

Obtain:

- turnover requirements;

- commissioning plan;

- quality-record index requirements;

- owner/Hydro-Québec acceptance requirements;

- system completion forms;

- test forms;

- certificates;

- manufacturer start-up reports;

- warranty requirements;

- O&M requirements;

- as-built requirements.

13.11.2 PLANNING

Build acceptance packages by system.

Example:

HVAC Equipment AHU-01

- approved submittal;

- receiving inspection;

- installation inspection;

- anchorage;

- duct/piping connections;

- insulation;

- electrical interface;

- controls;

- start-up;

- functional test;

- balancing;

- deficiencies;

- retests;

- final acceptance.

That package tells the whole story.

13.11.3 DOCUMENT CONTROL

Verify:

☐ latest final documents
☐ superseded records excluded/clearly identified
☐ test references correct
☐ equipment IDs consistent
☐ signatures complete
☐ index complete

13.11.4 MATERIAL / EQUIPMENT CONTROL

Confirm final installed equipment/material identification matches acceptance records.

13.11.5 INSPECTION / ACCEPTANCE REVIEW

Conduct final review:

Physical

Is system complete?

Documentary

Is evidence complete?

Testing

Did required tests pass?

Deficiencies

Are open issues controlled/closed?

Specialist acceptance

Is required sign-off present?

Turnover

Are O&M/as-builts/warranties available?

13.11.6 RECORDS / EVIDENCE

Acceptance evidence may include:

- inspection forms;

- test reports;

- commissioning sheets;

- start-up records;

- TAB reports;

- envelope test reports;

- fire/life-safety test records;

- electrical specialist reports;

- certificates;

- calibration certificates;

- photos;

- NCR/deficiency closure;

- manufacturer reports;

- as-builts;

- O&M manuals;

- warranties;

- final acceptance forms.

13.11.7 NC / DEFICIENCY

Common final-record gaps:

- missing test report;

- unsigned form;

- unresolved test failure;

- missing calibration;

- equipment tag mismatch;

- missing manufacturer startup;

- open deficiency;

- as-built inconsistency.

13.11.8 CORRECTIVE ACTION — EXAMPLE

System physically works, but required manufacturer start-up sheet is missing.

Do not assume:

“It works, so we're done.”

Track missing acceptance evidence → obtain valid manufacturer/startup documentation or repeat required activity if necessary → complete acceptance package.

Physical completion and documentary completion are both required.

13.11.9 VERIFICATION

Perform final package audit:

Requirement → inspection → test → failure history → corrective action → retest → acceptance → turnover evidence

Can the entire chain be reconstructed?

13.11.10 CLOSURE

System acceptance closes when:

☐ physical construction complete
☐ inspection complete
☐ required testing complete
☐ failed tests closed
☐ commissioning complete
☐ specialist acceptance complete
☐ deficiencies closed
☐ as-builts updated
☐ O&M available
☐ warranties/certificates available
☐ final evidence indexed/filed

13.11.11 REPORTING / ANALYSIS

Create system-status reporting:

| System | Physical Complete | Testing | Failed Tests | Commissioning | Records | Acceptance |
| --- | --- | --- | --- | --- | --- | --- |
| Domestic Water | ✓ | ✓ | 0 open | ✓ | ✓ | Ready |
| AHU-01 | ✓ | ✓ | 1 closed | ✓ | ✓ | Accepted |
| Emergency Lighting | ✓ | Pending | — | Pending | Partial | Open |

This gives the Responsable qualité/PM a useful turnover readiness view.

13.11.12 QUALITY CHECKPOINT

☐ Physical completion
☐ Inspection records
☐ Test records
☐ Calibration records
☐ Manufacturer start-up
☐ Functional testing
☐ Integrated testing where required
☐ Failed-test closure
☐ Retest evidence
☐ Specialist acceptance
☐ Deficiency closure
☐ As-builts
☐ O&M
☐ Warranty/certificates
☐ Final index/package

TESTING & COMMISSIONING — MASTER READINESS FLOW

This should become a high-level app workflow:

1 — IS THE SYSTEM BUILT?

☐ Installation complete
☐ Inspections complete
☐ Deficiencies controlled

↓

2 — IS IT READY TO TEST?

☐ Approved procedure
☐ Utilities
☐ Instruments
☐ Calibration
☐ Specialists
☐ Witnesses

↓

3 — TEST

☐ Perform
☐ Record actual result
☐ Pass / Fail

↓

IF FAIL

CONTROL → DOCUMENT → CORRECT → REINSPECT → RETEST

↓

4 — FUNCTIONAL / INTEGRATED TEST

Where required.

↓

5 — SPECIALIST ACCEPTANCE

Required technical authority signs/accepts.

↓

6 — ACCEPTANCE PACKAGE

☐ Inspection
☐ Tests
☐ Retests
☐ Commissioning
☐ Deficiencies
☐ As-builts/O&M

↓

SYSTEM ACCEPTED

PRACTICAL EXAMPLE — AHU FROM INSTALLATION TO ACCEPTANCE

This is a good example of how several modules now connect.

Stage 1 — Installation

Mechanical → HVAC Equipment

You verify:

- correct AHU;

- receiving condition;

- base;

- anchors;

- vibration isolation;

- clearances;

- duct/piping/drain interfaces.

Stage 2 — Mechanical testing

Pressure/leak/duct tests as required.

Stage 3 — Electrical interface

Electrical → Equipment Installation / Testing Interface

Authorized electrical personnel complete required electrical acceptance.

Stage 4 — Controls

BAS devices installed and documented.

Stage 5 — Start-up

Testing → Equipment Start-Up

Manufacturer/specialist performs start-up.

Stage 6 — Functional test

Does unit:

- start;

- stop;

- respond to controls;

- operate without abnormal condition?

Stage 7 — TAB

Specialist balancing.

Stage 8 — Failure

Suppose fan vibration exceeds acceptance requirement.

Your system does:

FAIL → control → document → specialist diagnosis → correction → restart → retest → pass

Stage 9 — Acceptance evidence

Package contains:

- approved submittal;

- receiving inspection;

- installation;

- pressure/leak records;

- electrical acceptance;

- start-up sheet;

- controls test;

- TAB;

- vibration correction;

- retest;

- final acceptance.

Now AHU-01 is not merely “installed.”

It is:

installed → inspected → tested → commissioned → corrected → retested → accepted → traceable.

That is proper system-quality closure.

13. TESTING, COMMISSIONING & SYSTEM ACCEPTANCE — MODULE COMPLETE

13.1 Test Readiness ✓
13.2 Test Documentation ✓
13.3 Mechanical Testing ✓
13.4 Electrical Testing Interfaces ✓
13.5 Building Envelope Testing ✓
13.6 Functional Testing ✓
13.7 Equipment Start-Up ✓
13.8 Integrated/System Testing ✓
13.9 Failed-Test Management ✓✓
13.10 Retesting ✓
13.11 Acceptance Evidence ✓✓

The two sections I would mark as especially important for your eventual daily management are 13.9 Failed-Test Management and 13.11 Acceptance Evidence, because those are where an inspector begins moving from simply witnessing tests to actually controlling the quality status of systems.

Yes. Section 14 is where the entire quality system closes the loop. Up to this point, we have been controlling requirements, materials, installation, testing, interfaces, and corrective actions. Closeout is where we prove that nothing significant is still unresolved and that the project can actually be handed over in a controlled state.

The governing principle here is:

Physical completion is not the same as quality completion.

A project area is only truly complete when:

deficiencies are resolved → NCs are closed → tests are complete → records are complete → as-builts are current → O&M/warranties/certificates are assembled → acceptance evidence is traceable → turnover is formally achieved.

14. DEFICIENCIES, COMPLETION & CLOSEOUT

Overall quality objective

Systematically identify, classify, assign, correct, reinspect and close all remaining quality issues while assembling the complete technical and documentary record required for final project acceptance and turnover.

The universal closeout workflow is:

Preparatory review → formal survey → classify → assign → correct → reinspect → close deficiencies → close NCs → close test results → finalize as-builts → finalize O&M/certificates/warranties → compile final quality records → turnover → acceptance

14.1 PREPARATORY DEFICIENCY REVIEW

Quality objective

Identify and correct obvious deficiencies internally before formal owner/consultant deficiency inspections, reducing the volume of formal punch-list items and improving turnover readiness.

This should happen before the formal deficiency survey.

14.1.1 REQUIREMENTS — WHERE TO GET THEM

🔵 Obtain:

- latest IFC/as-built-oriented drawings;

- specifications;

- room finish schedules;

- equipment schedules;

- door/hardware schedules;

- commissioning status;

- existing deficiency lists;

- NC register;

- test status;

- PIE/PRIE;

- contract turnover requirements;

- owner/Hydro-Québec acceptance requirements;

- previous inspection reports.

14.1.2 PLANNING

Organize preparatory reviews by:

building → zone → room → system → discipline

Do not walk randomly.

Suggested room/zone sequence:

Ceiling → walls → doors → floors → MEP devices → equipment → access → labeling → fire/life safety → housekeeping

For technical rooms:

equipment → supports → piping/ducts/trays → penetrations → labels → access → controls → tests

14.1.3 DOCUMENT CONTROL

Verify:

☐ latest drawings
☐ latest approved changes
☐ current deficiency list
☐ current NC list
☐ current test status
☐ current equipment/room schedules

14.1.4 MATERIAL CONTROL

At this stage, material control is mostly about verifying final installed materials are:

- correct;

- undamaged;

- complete;

- consistent with approved finish/equipment schedules.

14.1.5 INSPECTION

Look for:

- incomplete work;

- damaged finishes;

- missing hardware;

- missing labels;

- open penetrations;

- unresolved sealant;

- unpainted repairs;

- missing access panels;

- leaks;

- damaged insulation;

- missing firestop;

- equipment access issues;

- incomplete commissioning items;

- temporary work left in place;

- housekeeping deficiencies.

Goal

Catch as much as possible before the formal owner/consultant walkdown.

14.1.6 RECORDS / EVIDENCE

Capture:

- location;

- deficiency description;

- responsible trade;

- photo;

- status;

- target completion date.

This can start as an internal preparatory list.

14.1.7 NC / DEFICIENCY

Not everything found here needs to become a formal NCR.

Use actual CRT classification rules.

Typical output:

- minor deficiency;

- incomplete work;

- significant deficiency;

- potential NC;

- testing/documentation hold.

14.1.8 CORRECTIVE ACTION — EXAMPLE

During internal walkdown, you find 8 access panels missing above concealed valves.

Better to catch this internally than have Hydro-Québec list all 8 during formal turnover.

Identify → assign → install → verify actual access → close before formal survey.

14.1.9 VERIFICATION

Revisit corrected items before formal deficiency walk.

14.1.10 CLOSURE

Preparatory review closes when:

☐ area substantially complete
☐ obvious defects addressed
☐ temporary work removed where appropriate
☐ major tests complete or status known
☐ documentation gaps identified
☐ ready for formal survey

14.1.11 REPORTING / ANALYSIS

Track:

- preparatory deficiencies by trade;

- repeated defect type;

- area readiness;

- items likely to block formal acceptance.

14.1.12 QUALITY CHECKPOINT

☐ Area complete enough
☐ Visual quality
☐ Equipment complete
☐ Labels complete
☐ Access complete
☐ Firestop complete
☐ MEP complete
☐ Major tests status known
☐ Obvious defects corrected
☐ Ready for formal survey

14.2 FORMAL DEFICIENCY SURVEY

Quality objective

Conduct a systematic, traceable formal review of completed work with all required parties and capture every identified deficiency in a controlled register.

14.2.1 REQUIREMENTS

Obtain:

- contract acceptance requirements;

- turnover procedures;

- owner/consultant inspection protocol;

- latest drawings;

- approved changes;

- deficiency forms/platform;

- acceptance criteria.

14.2.2 PLANNING

Before survey:

- define zones;

- identify participants;

- ensure access;

- prepare plans;

- prepare deficiency numbering;

- confirm documentation method;

- decide how photos will be linked.

14.2.3 DOCUMENT CONTROL

Verify all participants are looking at current documents.

14.2.4 MATERIAL CONTROL

Not a major focus here except final installed-product conformity.

14.2.5 INSPECTION

Perform by fixed sequence.

For each item:

- identify location;

- describe deficiency precisely;

- identify system/trade;

- reference requirement where necessary;

- take photo;

- assign unique ID.

Weak

“Fix paint.”

Strong

“Room B-204, west wall beside Door D204: approximately 500 mm area of uneven paint finish and visible substrate repair; restore surface preparation and finish to match approved wall coating.”

14.2.6 RECORDS

Formal deficiency record should include:

- deficiency ID;

- date;

- location;

- discipline;

- description;

- responsible party;

- photo;

- priority/classification;

- target date;

- status;

- reinspection result.

14.2.7 NC / DEFICIENCY

Formal survey may identify conditions requiring escalation to NCR.

Do not automatically keep every issue as punch-list if technical significance is higher.

14.2.8 CORRECTIVE ACTION

Assign according to responsible trade/system.

14.2.9 VERIFICATION

Every formal deficiency requires actual reinspection before closure.

14.2.10 CLOSURE

Survey itself is complete when all observed items are captured in the register.

Individual items may remain open.

14.2.11 REPORTING / ANALYSIS

Track:

- total deficiencies;

- by trade;

- by area;

- by severity;

- by aging.

14.2.12 QUALITY CHECKPOINT

☐ Participants
☐ Current drawings
☐ Area inspected systematically
☐ IDs assigned
☐ Photos captured
☐ Responsible party assigned
☐ Register updated

14.3 DEFICIENCY CLASSIFICATION

Quality objective

Classify deficiencies consistently so priority, escalation, responsibility and closure effort match the actual significance of the issue.

The exact categories should follow CRT's system.

A generic framework could distinguish:

- cosmetic/minor;

- workmanship;

- incomplete work;

- functional;

- safety/life-safety;

- technical/non-conforming;

- documentation;

- commissioning;

- turnover-blocking.

Do not impose these labels if CRT uses different terminology.

14.3.1 REQUIREMENTS

Obtain:

- CRT deficiency classification rules;

- NCR procedure;

- risk/priority criteria;

- turnover acceptance criteria.

14.3.2 PLANNING

For each deficiency ask:

- Does it affect appearance only?

- Does it affect function?

- Does it affect safety?

- Does it violate contract requirement?

- Does it require professional disposition?

- Does it block testing?

- Does it block turnover?

14.3.3 DOCUMENT CONTROL

Use current classification procedure.

14.3.4 MATERIAL CONTROL

N/A.

14.3.5 INSPECTION / CLASSIFICATION

Classify based on evidence, not emotion.

14.3.6 RECORDS

Record classification and rationale where necessary.

14.3.7 NC / DEFICIENCY

If issue crosses NCR threshold, escalate per procedure.

14.3.8 CORRECTIVE ACTION

Classification affects urgency and approval path.

14.3.9 VERIFICATION

Ensure classification still appropriate if more information emerges.

14.3.10 CLOSURE

Classification complete when item has clear priority/path.

14.3.11 REPORTING / ANALYSIS

Useful for management dashboard.

14.3.12 QUALITY CHECKPOINT

☐ Issue understood
☐ Impact assessed
☐ Priority assigned
☐ NCR threshold considered
☐ Turnover impact considered
☐ Responsible path clear

14.4 ASSIGNMENT

Quality objective

Assign every deficiency to a clear responsible party with an owner, target date and required closure evidence.

Unassigned deficiency = likely forgotten deficiency.

14.4.1 REQUIREMENTS

Obtain:

- subcontractor responsibility matrix;

- project organization;

- deficiency workflow;

- contractual scope boundaries.

14.4.2 PLANNING

For every item determine:

- responsible contractor;

- responsible supervisor;

- required specialist;

- target completion;

- dependencies.

14.4.3 DOCUMENT CONTROL

Ensure item references correct drawing/spec/scope if responsibility disputed.

14.4.4 MATERIAL CONTROL

If correction needs replacement material, verify approved product.

14.4.5 INSPECTION / TRACKING

Monitor:

- assigned?

- acknowledged?

- planned?

- corrected?

- ready for reinspection?

14.4.6 RECORDS

Capture:

- assignee;

- target date;

- comments;

- progress status.

14.4.7 NC / DEFICIENCY

Escalate unowned/disputed items.

14.4.8 CORRECTIVE ACTION

Clarify scope or management assignment.

14.4.9 VERIFICATION

Ensure responsible party actually addresses correct item.

14.4.10 CLOSURE

Assignment complete once responsibility and date are clear.

14.4.11 REPORTING / ANALYSIS

Track overdue items by subcontractor.

14.4.12 QUALITY CHECKPOINT

☐ Responsible party
☐ Owner/contact
☐ Target date
☐ Scope clear
☐ Dependencies known
☐ Status visible

14.5 CORRECTIVE WORK

Quality objective

Ensure deficiency corrections restore the work to the actual project requirement without creating new defects or masking the original issue.

14.5.1 REQUIREMENTS

Use:

- original requirement;

- approved repair procedure;

- manufacturer instructions;

- professional disposition;

- NCR corrective action;

- current drawings.

14.5.2 PLANNING

Before correction:

- understand root condition;

- identify affected adjacent work;

- determine whether repair needs approval;

- plan access/protection;

- determine retesting requirement.

14.5.3 DOCUMENT CONTROL

Verify current repair/detail.

14.5.4 MATERIAL CONTROL

Check repair materials are approved and compatible.

14.5.5 INSPECTION

Observe where necessary:

- removal/preparation;

- repair method;

- installed material;

- protection;

- curing;

- final finish.

14.5.6 RECORDS

Capture:

before → during → after

for significant corrections.

14.5.7 NC / DEFICIENCY

Correction itself can be deficient.

Example:

membrane patch applied over dirty substrate.

14.5.8 CORRECTIVE ACTION — EXAMPLE

Damaged waterproofing repaired, but protection board not reinstated.

Do not close at membrane repair alone.

The full system must be restored.

14.5.9 VERIFICATION

Check entire affected assembly.

14.5.10 CLOSURE

Corrective work ready for reinspection when:

☐ repair complete
☐ adjacent systems restored
☐ required cure complete
☐ required test ready/completed
☐ evidence available

14.5.11 REPORTING / ANALYSIS

Track repeated repairs of same defect type.

14.5.12 QUALITY CHECKPOINT

☐ Correct requirement
☐ Approved repair
☐ Correct material
☐ Preparation
☐ Execution
☐ Adjacent work protected/restored
☐ Testing if required
☐ Ready for reinspection

14.6 REINSPECTION

Quality objective

Independently verify that corrective work actually resolves the original deficiency and that no new unacceptable condition was created.

14.6.1 REQUIREMENTS

Review:

- original deficiency;

- original photo;

- requirement;

- corrective action;

- repair method;

- test requirement.

14.6.2 PLANNING

Reinspect exact location.

Do not rely on contractor message saying “done.”

14.6.3 DOCUMENT CONTROL

Confirm correct deficiency ID.

14.6.4 MATERIAL CONTROL

Verify repaired materials where relevant.

14.6.5 INSPECTION

Ask:

- Was original problem corrected?

- Does correction meet requirement?

- Did repair affect adjacent work?

- Does function need retesting?

- Is documentation complete?

14.6.6 RECORDS

Capture:

- reinspection date;

- inspector;

- result;

- after photo;

- comments;

- reopen if failed.

14.6.7 NC / DEFICIENCY

If correction insufficient:

REJECT / REOPEN

Do not create a new deficiency unless process requires it; maintain traceability to original item.

14.6.8 CORRECTIVE ACTION

Return to responsible trade.

14.6.9 VERIFICATION

Repeat after next correction.

14.6.10 CLOSURE

Only when actual acceptance condition achieved.

14.6.11 REPORTING / ANALYSIS

Track first-pass closure rate.

Low first-pass closure may indicate poor corrective workmanship.

14.6.12 QUALITY CHECKPOINT

☐ Original deficiency reviewed
☐ Exact location reinspected
☐ Correction complete
☐ Adjacent work acceptable
☐ Functional retest if required
☐ After photo
☐ Accept / reopen

14.7 CLOSURE

Quality objective

Close deficiencies only when compliance has been physically verified and required evidence is complete.

A useful closure rule:

“Done” is contractor status. “Closed” is verified quality status.

14.7.1 REQUIREMENTS

Follow CRT closure procedure.

14.7.2 PLANNING

Clear backlog systematically by:

- high priority;

- turnover blocking;

- aging;

- area;

- subcontractor.

14.7.3 DOCUMENT CONTROL

Ensure final record references correct item.

14.7.4 MATERIAL CONTROL

N/A unless repair product relevant.

14.7.5 INSPECTION

Physical verification required where appropriate.

14.7.6 RECORDS

Minimum:

- deficiency ID;

- original issue;

- correction;

- after evidence;

- reinspection date;

- closed by;

- closure date.

14.7.7 NC / DEFICIENCY

Do not close unresolved dependency.

Example:

ceiling tile replaced but roof leak causing stain remains unresolved.

Root issue remains open.

14.7.8 CORRECTIVE ACTION

Reopen if incomplete.

14.7.9 VERIFICATION

Final closure review.

14.7.10 CLOSURE

☐ correction verified
☐ related test complete
☐ evidence complete
☐ dependencies resolved
☐ register updated

14.7.11 REPORTING / ANALYSIS

Track:

- open;

- ready for reinspection;

- closed;

- overdue.

14.7.12 QUALITY CHECKPOINT

☐ Physical fix
☐ Verification
☐ Retest if required
☐ Evidence
☐ Status updated
☐ Dependencies closed

14.8 OUTSTANDING NC CLOSURE

Quality objective

Ensure every formal non-conformance reaches an approved disposition, corrective action, verification and documented closure before final turnover unless explicitly accepted otherwise by authorized parties.

14.8.1 REQUIREMENTS

Obtain:

- NC register;

- NCR procedure;

- dispositions;

- professional instructions;

- corrective actions;

- test records;

- closeout requirements.

14.8.2 PLANNING

Review each NC:

- open?

- disposition approved?

- work corrected?

- test required?

- professional acceptance required?

- dependent work affected?

14.8.3 DOCUMENT CONTROL

Keep full chain:

NC → disposition → corrective action → evidence → verification → acceptance → closure

14.8.4 MATERIAL CONTROL

Verify replacement/repair materials.

14.8.5 INSPECTION

Inspect implemented disposition.

14.8.6 RECORDS

Retain all associated documents.

14.8.7 NC / DEFICIENCY

An NCR cannot be closed simply because construction moved on.

14.8.8 CORRECTIVE ACTION — EXAMPLE

Misplaced anchor accepted through engineered disposition with additional reinforcement/connection modification.

Closure requires:

- approved disposition;

- modification completed;

- inspection;

- required test;

- professional acceptance.

14.8.9 VERIFICATION

Confirm all disposition conditions satisfied.

14.8.10 CLOSURE

☐ disposition approved
☐ correction implemented
☐ inspection complete
☐ test complete
☐ specialist/professional acceptance
☐ records complete
☐ NCR formally closed

14.8.11 REPORTING / ANALYSIS

Track aged/open NCs as major turnover risk.

14.8.12 QUALITY CHECKPOINT

☐ NC ID
☐ Disposition
☐ Corrective action
☐ Verification
☐ Test
☐ Professional acceptance
☐ Closure signature/status

14.9 OUTSTANDING TEST RESULTS

Quality objective

Ensure no system is treated as accepted while required test results remain missing, pending, failed or unreviewed.

14.9.1 REQUIREMENTS

Obtain:

- test register;

- commissioning matrix;

- PIE/PRIE;

- laboratory results;

- specialist reports;

- pending cylinder strengths;

- electrical/mechanical/envelope test status.

14.9.2 PLANNING

Create status:

Required → Scheduled → Tested → Result Pending → Pass → Fail → Retest → Accepted

14.9.3 DOCUMENT CONTROL

Verify every required test has a traceable result.

14.9.4 MATERIAL CONTROL

N/A.

14.9.5 INSPECTION / TEST REVIEW

Review:

- missing tests;

- pending lab results;

- failed tests;

- test reports not signed;

- retest not received.

14.9.6 RECORDS

Maintain master test register.

14.9.7 NC / DEFICIENCY

Missing/pending test can itself be a turnover hold.

14.9.8 CORRECTIVE ACTION

Obtain result, perform missing test, or retest as required.

14.9.9 VERIFICATION

Confirm final acceptance.

14.9.10 CLOSURE

☐ every required test accounted for
☐ pending results received
☐ fails closed
☐ specialist approvals complete

14.9.11 REPORTING / ANALYSIS

Track testing blockers by system.

14.9.12 QUALITY CHECKPOINT

☐ Test required
☐ Test performed
☐ Result received
☐ Pass/fail
☐ Retest
☐ Specialist acceptance
☐ Turnover status

14.10 REDLINES / AS-BUILTS

Quality objective

Ensure final record drawings accurately reflect installed construction, including approved field changes and actual routing/location of systems where required.

14.10.1 REQUIREMENTS

Obtain:

- as-built requirements;

- drawing conventions;

- field redline procedure;

- survey requirements;

- model/BIM requirements;

- turnover format.

14.10.2 PLANNING

Do not wait until project end to reconstruct changes from memory.

Update continuously.

Track:

- utility routes;

- penetrations;

- equipment locations;

- changed dimensions;

- relocated services;

- revised connections;

- owner-directed changes.

14.10.3 DOCUMENT CONTROL

Ensure redlines are based on correct latest drawing.

14.10.4 MATERIAL CONTROL

N/A.

14.10.5 INSPECTION / VERIFICATION

Cross-check record drawings against actual field condition.

For buried/concealed work, use survey/photos/installation records.

14.10.6 RECORDS

Outputs:

- redlined drawings;

- surveys;

- final as-built drawings;

- BIM/model updates where required;

- supporting field records.

14.10.7 NC / DEFICIENCY

Typical:

- missing changes;

- contradictory revisions;

- inaccurate buried utility route;

- equipment tags inconsistent.

14.10.8 CORRECTIVE ACTION

Correct record drawings using valid evidence.

14.10.9 VERIFICATION

Final field-document reconciliation.

14.10.10 CLOSURE

☐ field changes captured
☐ surveys incorporated
☐ equipment locations current
☐ concealed work documented
☐ final as-built package accepted

14.10.11 REPORTING / ANALYSIS

Track missing as-built information early.

14.10.12 QUALITY CHECKPOINT

☐ Current base drawing
☐ Changes captured
☐ Buried utilities
☐ Equipment
☐ Penetrations
☐ Dimensions/elevations
☐ Survey
☐ Final review
☐ Submission

14.11 O&M DOCUMENTATION

Quality objective

Provide complete, accurate operation and maintenance information for installed systems and equipment so the owner can operate, inspect, maintain and troubleshoot the facility after turnover.

14.11.1 REQUIREMENTS

Obtain:

- O&M manual requirements;

- equipment schedules;

- approved submittals;

- commissioning requirements;

- owner templates;

- digital filing requirements.

14.11.2 PLANNING

Build O&M packages progressively by system/equipment.

Typical contents:

- equipment data;

- manufacturer manuals;

- maintenance instructions;

- spare parts;

- recommended maintenance;

- startup/shutdown;

- troubleshooting;

- controls sequences;

- final settings where required;

- contact information.

14.11.3 DOCUMENT CONTROL

Verify:

☐ equipment model matches installed unit
☐ current manufacturer manual
☐ approved submittal matches final product
☐ obsolete manuals removed

14.11.4 MATERIAL CONTROL

Verify physical equipment/accessories/spares align with documentation.

14.11.5 INSPECTION / REVIEW

Check O&M package against physical installation.

14.11.6 RECORDS

Final O&M manuals / digital files.

14.11.7 NC / DEFICIENCY

Common:

- generic manual;

- wrong model;

- missing maintenance instructions;

- missing controls documentation;

- incomplete equipment list.

14.11.8 CORRECTIVE ACTION

Obtain correct documentation.

14.11.9 VERIFICATION

Cross-check equipment tag/model/serial where appropriate.

14.11.10 CLOSURE

☐ all systems represented
☐ correct equipment manuals
☐ maintenance info
☐ controls info
☐ owner format satisfied
☐ submitted/accepted

14.11.11 REPORTING / ANALYSIS

Track missing manuals by equipment/vendor.

14.11.12 QUALITY CHECKPOINT

☐ Equipment list
☐ Manufacturer manual
☐ Model match
☐ Maintenance
☐ Operation
☐ Troubleshooting
☐ Controls
☐ Spare parts
☐ Final submission

14.12 CERTIFICATES / TECHNICAL RECORDS

Quality objective

Assemble all certificates, inspection reports, test results and specialist technical records required to demonstrate contractual and regulatory compliance.

14.12.1 REQUIREMENTS

Examples may include:

- material certificates;

- concrete test results;

- welding/NDT reports;

- firestop documentation;

- equipment startup certificates;

- electrical specialist reports;

- mechanical testing;

- balancing reports;

- roofing warranty inspections;

- calibration certificates;

- professional sign-offs.

Actual list comes from project requirements.

14.12.2 PLANNING

Create document matrix:

Required document → responsible party → due date → received → reviewed → accepted

14.12.3 DOCUMENT CONTROL

Verify:

- correct project;

- correct equipment/system;

- correct revision;

- signatures;

- dates;

- referenced standards/procedures where required.

14.12.4 MATERIAL CONTROL

Cross-check certificates against installed materials.

14.12.5 INSPECTION / REVIEW

Ensure technical record corresponds to actual installed work.

14.12.6 RECORDS

Compile indexed technical records.

14.12.7 NC / DEFICIENCY

Missing/incorrect certificate can block acceptance.

14.12.8 CORRECTIVE ACTION

Obtain corrected certificate/report or repeat required activity where necessary.

14.12.9 VERIFICATION

Final document audit.

14.12.10 CLOSURE

☐ required certificate list complete
☐ all received
☐ traceable
☐ signed
☐ accepted
☐ indexed

14.12.11 REPORTING / ANALYSIS

Track document completeness percentage.

14.12.12 QUALITY CHECKPOINT

☐ Document requirement
☐ Responsible party
☐ Received
☐ Correct system/material
☐ Signed
☐ Valid
☐ Accepted
☐ Filed

14.13 WARRANTIES

Quality objective

Ensure required warranties are complete, valid, accurately identify the installed systems and have appropriate commencement conditions and supporting documentation.

14.13.1 REQUIREMENTS

Obtain:

- contract warranty requirements;

- manufacturer warranties;

- contractor warranties;

- roofing warranties;

- equipment warranty terms;

- start dates;

- maintenance conditions.

14.13.2 PLANNING

Build warranty register:

| System | Vendor | Duration | Start Date | Document | Status |
| --- | --- | --- | --- | --- | --- |

14.13.3 DOCUMENT CONTROL

Check:

- correct project;

- product/model;

- duration;

- commencement;

- signatures;

- exclusions;

- required registration.

14.13.4 MATERIAL CONTROL

Verify warranty corresponds to installed product.

14.13.5 INSPECTION / REVIEW

Ensure prerequisites for warranty have been met.

Example:

- manufacturer inspection;

- startup;

- maintenance;

- approved installer.

14.13.6 RECORDS

Warranty register + warranty documents.

14.13.7 NC / DEFICIENCY

Typical:

- wrong product;

- incorrect start date;

- missing registration;

- incomplete manufacturer inspection.

14.13.8 CORRECTIVE ACTION

Resolve administrative/technical prerequisite.

14.13.9 VERIFICATION

Confirm final valid warranty.

14.13.10 CLOSURE

☐ all required warranties
☐ correct installed products
☐ valid duration
☐ start date established
☐ owner receives documents

14.13.11 REPORTING / ANALYSIS

Track outstanding warranties.

14.13.12 QUALITY CHECKPOINT

☐ System
☐ Vendor
☐ Product
☐ Warranty period
☐ Start date
☐ Registration
☐ Required inspection
☐ Final document

14.14 FINAL QUALITY RECORDS

Quality objective

Compile the final auditable quality record showing how the project requirements were controlled from construction through testing, correction and acceptance.

This is essentially the QMS evidence package.

14.14.1 REQUIREMENTS

Obtain project record index requirements.

Potential categories:

- Plan Qualité;

- PIE/PRIE;

- inspections;

- material approvals;

- certificates;

- test reports;

- photographs;

- NCs;

- corrective actions;

- deficiency closure;

- surveys;

- as-builts;

- commissioning;

- O&M;

- warranties.

14.14.2 PLANNING

Organize by:

discipline → system → area → document type

or whatever CRT's official structure requires.

Consistency is more important than a clever structure.

14.14.3 DOCUMENT CONTROL

Final audit:

- correct revisions;

- complete metadata;

- no unexplained duplicates;

- superseded docs clearly identified;

- signatures;

- traceable references.

14.14.4 MATERIAL CONTROL

Cross-check material records against installed work.

14.14.5 INSPECTION / RECORD AUDIT

Ask:

If someone audited this system six months from now, could they reconstruct how it was accepted?

For each system:

requirement → material → inspection → test → issue → correction → retest → acceptance

14.14.6 RECORDS / OUTPUTS

Final indexed quality dossier.

14.14.7 NC / DEFICIENCY

Record gaps become closeout deficiencies.

14.14.8 CORRECTIVE ACTION

Recover/complete valid evidence.

Never manufacture missing records.

14.14.9 VERIFICATION

Independent final record audit where required.

14.14.10 CLOSURE

☐ index complete
☐ records traceable
☐ inspections complete
☐ tests complete
☐ NCs closed
☐ deficiencies closed
☐ as-builts complete
☐ commissioning complete
☐ O&M complete
☐ warranties complete

14.14.11 REPORTING / ANALYSIS

Report dossier completeness by system/discipline.

14.14.12 QUALITY CHECKPOINT

☐ Inspection records
☐ Material approvals
☐ Certificates
☐ Tests
☐ NC closure
☐ Deficiency closure
☐ Photos
☐ As-builts
☐ Commissioning
☐ O&M
☐ Warranties
☐ Final index

14.15 TURNOVER / ACCEPTANCE

This is the final project-quality gate.

Quality objective

Transfer the completed facility/system to the owner with physical work, testing, documentation, training and outstanding items controlled in accordance with contractual acceptance requirements.

14.15.1 REQUIREMENTS

Obtain:

- contractual turnover procedure;

- substantial/final completion requirements;

- owner/Hydro-Québec acceptance requirements;

- turnover checklists;

- commissioning completion requirements;

- training requirements;

- keys/access/security requirements;

- spare parts;

- O&M;

- warranties;

- final quality dossier.

14.15.2 PLANNING

Prepare turnover by:

- area;

- system;

- milestone;

- package.

For each turnover package ask:

Physical complete?
Tested?
Commissioned?
Deficiencies closed?
NCs closed?
Documents complete?
Training complete?

14.15.3 DOCUMENT CONTROL

Verify final:

- drawings;

- manuals;

- test reports;

- certificates;

- warranties;

- acceptance forms.

14.15.4 MATERIAL CONTROL

Verify:

- spare parts;

- special tools;

- keys;

- consumables;

- attic stock where required.

14.15.5 INSPECTION / ACCEPTANCE REVIEW

Final walkdown should confirm:

Physical

- complete;

- clean;

- operational;

- no unresolved damage.

Systems

- tests passed;

- commissioning complete;

- identification complete.

Documentation

- as-builts;

- O&M;

- certificates;

- warranties.

Operational readiness

- access;

- maintainability;

- training;

- spares/tools.

14.15.6 RECORDS / EVIDENCE

Outputs may include:

- turnover checklist;

- final deficiency list;

- owner acceptance form;

- training records;

- key/tool/spares handover;

- document transmittals;

- final quality dossier.

14.15.7 NC / DEFICIENCY

If minor items remain, contractual procedure determines whether turnover can proceed with outstanding-list controls.

Do not assume unresolved critical/life-safety issues can be deferred.

14.15.8 CORRECTIVE ACTION — EXAMPLE

Everything physical is complete, but final fire-alarm integrated test report is missing.

Turnover status should show that dependency clearly.

Do not mark system fully accepted simply because the field work is complete.

14.15.9 VERIFICATION

Final verification:

physical + functional + documentary + contractual

14.15.10 CLOSURE

Final quality acceptance when:

☐ construction complete
☐ formal deficiencies closed/controlled
☐ NCs closed
☐ tests complete
☐ commissioning complete
☐ integrated tests complete where required
☐ as-builts complete
☐ O&M complete
☐ certificates complete
☐ warranties complete
☐ training complete where required
☐ final quality records accepted
☐ owner acceptance documented

14.15.11 REPORTING / ANALYSIS

Final turnover dashboard can show:

| System/Area | Physical | Deficiencies | NC | Testing | Docs | Acceptance |
| --- | --- | --- | --- | --- | --- | --- |
| Area A | ✓ | Closed | Closed | ✓ | ✓ | Accepted |
| Area B | ✓ | 3 Open | Closed | ✓ | Partial | Pending |
| AHU-01 | ✓ | Closed | — | ✓ | ✓ | Accepted |
| Fire Alarm | ✓ | Closed | — | Pending report | Partial | Hold |

This provides actual project-readiness visibility.

14.15.12 FINAL TURNOVER QUALITY CHECKPOINT

PHYSICAL COMPLETION

☐ Work complete
☐ Final cleaning
☐ No unresolved damage
☐ Access maintained
☐ Equipment identified

QUALITY

☐ Deficiencies closed
☐ NCRs closed
☐ Corrective actions verified

TESTING

☐ Tests complete
☐ Failed tests closed
☐ Retests passed
☐ Commissioning complete
☐ Integrated testing complete

RECORDS

☐ As-builts
☐ O&M
☐ Certificates
☐ Technical records
☐ Warranties
☐ Inspection records
☐ Test records

OWNER READINESS

☐ Training
☐ Spares
☐ Keys/access
☐ Special tools
☐ Final transmittals

ACCEPTANCE

☐ Required professionals/specialists accepted
☐ Responsable qualité confirms package status
☐ Owner/client acceptance documented
☐ Turnover package complete

CLOSEOUT MASTER FLOW

This should eventually become one of the high-level process maps in the app:

1. INTERNAL PREPARATORY REVIEW

Find problems before the formal walk.

↓

2. FORMAL DEFICIENCY SURVEY

Capture every issue.

↓

3. CLASSIFY & ASSIGN

Who owns it?
How important is it?
Does it block turnover?

↓

4. CORRECT

Perform approved corrective work.

↓

5. REINSPECT

Don't close from email.

↓

6. CLOSE DEFICIENCIES

Verified physical closure.

↓

7. CLOSE NCRs

Disposition + correction + verification + acceptance.

↓

8. CLOSE TESTING

No missing/pending/failed tests.

↓

9. RECORD DOCUMENTS

Redlines → as-builts.

↓

10. TURNOVER DOCUMENTATION

O&M → certificates → technical records → warranties.

↓

11. FINAL QUALITY DOSSIER

Everything indexed and traceable.

↓

12. TURNOVER / ACCEPTANCE

PRACTICAL EXAMPLE — ONE AREA AT CLOSEOUT

Imagine an electrical room looks physically finished.

A casual view says:

“Room complete.”

Your closeout system asks:

Architectural

- paint finished?

- doors/hardware operational?

- floor complete?

- sealants finished?

Mechanical

- ventilation operational?

- dampers accessible?

- labels complete?

Electrical

- equipment installed?

- labels complete?

- specialist tests accepted?

Fire/life safety

- penetrations firestopped?

- rated door accepted?

- fire alarm interfaces complete?

Multidisciplinary

- maintenance clearances maintained?

- access panels usable?

Testing

- every required test result available?

Deficiencies

- all items actually reinspected?

NCs

- any formal NC still open?

Documentation

- final equipment location captured?

- O&M present?

- warranties?

- certificates?

Only when those all align is:

Electrical Room X = QUALITY COMPLETE / TURNOVER READY

That is the difference between “construction appears finished” and controlled project closeout.

BUILD 2 — DEFICIENCIES, COMPLETION & CLOSEOUT STATUS

14.1 Preparatory Deficiency Review ✓
14.2 Formal Deficiency Survey ✓
14.3 Deficiency Classification ✓
14.4 Assignment ✓
14.5 Corrective Work ✓
14.6 Reinspection ✓
14.7 Closure ✓
14.8 Outstanding NC Closure ✓✓
14.9 Outstanding Test Results ✓✓
14.10 Redlines / As-Builts ✓
14.11 O&M Documentation ✓
14.12 Certificates / Technical Records ✓
14.13 Warranties ✓
14.14 Final Quality Records ✓✓
14.15 Turnover / Acceptance ✓✓

And with this, the main Build 2 field-content architecture is essentially complete from earthworks all the way through turnover. The next valuable step is not adding random more technical content; it is converting all of these sections into a usable app/QMS structure with common templates, inspection gates, status logic, cross-references, and daily field workflows so this becomes something you can actually navigate on site rather than a giant manual.