BUILD 3 – LINKS

Yep. We start the actual matrix now.

I’m treating Build 2 as the authority for activity names and relationships rather than inventing a generic construction sequence. For example, Build 2 explicitly defines Section 1 as seven activities and gives the integrated Substructure sequence as Formwork → Reinforcement → Embedded Items → Pre-Pour Gate → Foundation Concrete → Acceptance → Walls/Slab → Waterproofing → Insulation → Drainage → Backfill.

For Build 3, I’m also going to use activity IDs rather than prose wherever possible. That will make these links directly convertible into application data later.

BUILD 3 — MASTER CROSS-LINK MATRIX

Part 1 — Sections 1–3

1. SITEWORK & EARTHWORKS

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1 | Existing Conditions | — | 1.2, 1.3, 12.x | Civil, Structural, Existing Utilities, Adjacent Property | Existing-condition records, photos, protection | Baseline survey / condition verification where required | Existing conditions before disturbance |
| 1.2 | Survey & Layout | 1.1 | 1.3, 1.4, 2.x, 3.x, 12.x | Civil, Structural, Architectural, M/E | Control points, benchmarks, gridlines, elevations | Survey verification | Layout/control before excavation or permanent work |
| 1.3 | Excavation | 1.1, 1.2 | 1.4, 2.x, 12.2 | Geotechnical, Structural, Civil, Utilities, Drainage | Excavation limits, bottom condition, groundwater, protection | Survey; geotechnical verification | Bottom of excavation before granular/concrete/foundation work |
| 1.4 | Subgrade | 1.3 | 1.5, 2.8, 12.5 | Geotechnical, Civil, Structural | Bearing condition, elevation, moisture, unsuitable material | Geotechnical acceptance; proofing/testing where specified | Subgrade before granular/base |
| 1.5 | Granular Materials | 1.4 | 1.6, 2.8, 12.5 | Geotechnical, Civil, Structural, Drainage | Material approval, lifts, moisture, grading | Density/compaction testing | Individual lifts before subsequent lift/concealment |
| 1.6 | Backfill | 1.4/1.5 as applicable; buried work accepted | Final grading, 12.x | Civil, Structural, Underground M/E, Drainage, Waterproofing | Material, lifts, protection of buried work | Density/compaction testing | Buried services/assemblies before backfill |
| 1.7 | Site Drainage | 1.2, 1.3, 1.4/1.5 as applicable | 1.6, 12.3, 12.5, 12.6 | Civil, Plumbing/Mechanical, Site Grading | Bedding, slope, joints, structures, connections | Survey; leakage/watertightness where specified | Pipe, bedding, connections and invert data before backfill |

Build 2 explicitly treats Excavation → Subgrade → Granular → Drainage → Backfill as a controlled sequence in which acceptance of one condition enables the next, including a pre-concealment gate before buried drainage disappears.

2. SUBSTRUCTURE

The source explicitly establishes the integrated sequence here rather than treating these pages independently.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 | Foundation Formwork | 1.2, 1.3, 1.4 | 2.2, 2.3, 2.4 | Structural, Survey, Architectural, M/E | Geometry, elevation, stability, openings, joints/waterstops | Survey/dimensional verification | Form condition before concrete |
| 2.2 | Foundation Reinforcement | 2.1; approved reinforcing material | 2.3, 2.4 | Structural, M/E embeds, Grounding | Bar size, spacing, laps, cover, supports, dowels | Reinforcement inspection | Complete reinforcement before pour |
| 2.3 | Embedded Items | 2.1, 2.2 | 2.4, 2.5, future M/E/equipment | Structural, Mechanical, Electrical, Architectural | Anchor bolts, sleeves, conduits, plates, blockouts, waterstops | Survey/dimensional verification where required | All cast-in items before pour |
| 2.4 | Pre-Pour Quality Gate | 2.1, 2.2, 2.3 | 2.5 | Structural + M/E + Survey + Quality | Formwork, rebar, embeds, cleanliness, releases | Hold/witness points; required pre-pour acceptance | Primary foundation concealment gate |
| 2.5 | Foundation Concrete | 2.4 released | 2.6, 2.7, 2.9 | Structural, Testing Agency, Survey, M/E embeds | Mix, delivery, placement, consolidation, finish, curing | Concrete testing | Embedded work becomes permanently concealed |
| 2.6 | Foundation Concrete Acceptance | 2.5; curing/testing sufficiently complete | 2.7, 2.9, 2.10, 2.11, 2.12, 3.x | Structural, Survey, Testing Agency | Geometry, surfaces, anchors/openings, defects/repairs | Strength results; dimensional acceptance | — |
| 2.7 | Foundation Walls | 2.1–2.6 logic as applicable | 2.9, 2.10, 2.11, 2.12 | Structural, Envelope, M/E | Formwork, rebar, embeds, joints, waterstops, penetrations | Concrete testing/acceptance | Rebar + embeds + waterstops before pour |
| 2.8 | Slab-on-Grade | 1.4, 1.5; subbase accepted | 7.1, 7.2, equipment installation | Structural, Mechanical, Electrical, Architectural | Insulation, vapour barrier, rebar, drains, sleeves, conduits, embeds | Concrete tests; survey; specified slab testing | Vapour barrier + rebar + M/E + embeds before pour |
| 2.9 | Below-Grade Waterproofing | 2.6/2.7; substrate accepted | 2.10, 2.12 | Envelope, Structural, Mechanical/Electrical penetrations | Substrate, membrane, laps, terminations, penetrations, protection | Waterproofing testing where specified | Entire membrane before insulation/protection/backfill |
| 2.10 | Foundation Insulation | 2.9 where assembly requires waterproofing first | 2.12 | Envelope, Structural | Product, thickness, continuity, attachment, compatibility | Inspection/acceptance | Before backfill |
| 2.11 | Foundation Drainage | 1.4/1.5; foundation geometry available | 2.12, 1.7/12.x drainage | Civil, Plumbing/Mechanical, Structural, Waterproofing | Pipe, slope, granular surround, geotextile, cleanouts, outlet | Survey; drainage testing where specified | Entire drainage system before backfill |
| 2.12 | Backfill Against Structure | 2.6/2.7 + 2.9 + 2.10 + 2.11 accepted as applicable | Site grading / 12.x | Structural, Waterproofing, Insulation, Drainage, Civil | Protection of accepted assemblies, lifts, equipment access | Compaction/density testing | Final pre-backfill gate |

That last row is deliberately a multi-parent dependency. Build 2 specifically says that before backfill the system asks whether the operation could damage what was just accepted and requires concrete, waterproofing and insulation acceptance, with foundation drainage also requiring pre-backfill evidence.

And 2.4 is a genuine Gate node, not simply another inspection page: Build 2 explicitly states that concrete must not be placed until prerequisite quality conditions have been satisfied or formally released.

3. SUPERSTRUCTURE

Build 2 identifies the superstructure objective around material approval, geometry, installation, inspection/testing and load-path completion, while specifically noting interfaces with future steel, MEP and envelope systems.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3.1 | Cast-in-Place Concrete | Accepted supports/foundations; form/rebar/embeds/pre-pour controls | 3.2/3.3 interfaces; 4.x; 6.x; M/E rough-ins | Structural, Mechanical, Electrical, Envelope, Survey | Formwork, reinforcement, embeds, openings, temporary support, curing | Concrete testing; survey; structural acceptance | Rebar + embeds + sleeves + conduits + openings before pour |
| 3.2 | Structural Steel — Materials | Approved fabrication/shop documents | 3.3 | Structural, Supplier/Fabricator, Coatings | Member ID, grade, certificates, damage, coating, storage | Material/fabrication records | — |
| 3.3 | Structural Steel — Erection | 2.6 / accepted supports; 3.2; anchor survey | 3.4, 3.5, 3.6, 4.x, roof/M&E interfaces | Structural, Survey, Architectural, Envelope, M/E | Member location, orientation, plumb, elevation, temporary bracing, connections | Survey; connection inspection | Connections/areas becoming inaccessible |
| 3.4 | Bolted Connections | 3.2, 3.3 | Structural acceptance; 3.6; enclosure/MEP work | Structural Steel, Inspection Agency | Bolt grade, configuration, nuts/washers, tightening | Bolt inspection/testing per project requirements | Connections before covering/fireproofing where applicable |
| 3.5 | Welding | 3.2, 3.3 | Structural acceptance; 3.6 | Structural Steel, Testing/NDT Agency | WPS, welder qualification, joint prep, consumables, environmental conditions | VT/NDT — MT/PT/UT/RT as specified | Welds before coating/fireproofing/concealment |
| 3.6 | Steel Protection | 3.3; 3.4/3.5 complete as applicable | 4.x, 5.x, 6.x | Structural, Envelope, Fire/Life Safety, Finishes | Galvanizing, protective coatings, fireproofing, repair | DFT/thickness/adhesion etc. where specified | Protection in locations becoming inaccessible |
| 3.7 | Structural Masonry | Accepted support; approved materials | 4.x, 6.x, M/E interfaces | Structural, Architectural, Mechanical, Electrical, Fire/Life Safety | Units, mortar, grout, reinforcement, anchors, lintels, openings | Masonry/grout testing as required | Reinforcement + anchors + embeds + penetrations before grout/concealment |
| 3.8 | Precast Elements — If Applicable | Accepted supports/anchors; approved fabrication | Connections; envelope/interior/MEP interfaces | Structural, Survey, Envelope, Architectural | Member ID, damage, bearing, connections, grout, repairs | Fabrication records; erection survey; connection/grout inspection | Connections/grout/embeds before inaccessible |

The source explicitly establishes 3.2 → 3.3: steel materials must be accepted and ready for erection, and erection itself requires accepted concrete foundations/supports and verified anchors.

Likewise, 3.4 and 3.5 are child-quality processes of 3.3 rather than unrelated activities: erection requires complete connections, while the following pages separately control bolted connections and welding. Welding then explicitly connects to NDT where required.

And 3.6 must sit downstream of connection work because its own planning identifies connection areas, weld-repair zones and areas that will later become inaccessible.

Cross-System Links Established So Far

Now the useful part. These aren't duplicates of the tables—they are the graph edges that cross section boundaries:

| From | ↔ / → | To |
| --- | --- | --- |
| 1.2 Survey & Layout | → | 1.3 Excavation |
| 1.2 Survey & Layout | → | 2.1 Foundation Formwork |
| 1.2 Survey & Layout | ↔ | 2.3 Embedded Items |
| 1.2 Survey & Layout | ↔ | 3.3 Structural Steel Erection |
| 1.3 Excavation | → | 1.4 Subgrade |
| 1.3 Excavation | → | 2.x Foundation Work |
| 1.4 Subgrade | → | 1.5 Granular |
| 1.4 + 1.5 | → | 2.8 Slab-on-Grade |
| 1.5 Granular | → | 2.8 Slab-on-Grade |
| 1.6 Backfill | ↔ | 2.12 Backfill Against Structure |
| 1.7 Site Drainage | ↔ | 2.11 Foundation Drainage |
| 2.1 Formwork | → | 2.4 Pre-Pour Gate |
| 2.2 Reinforcement | → | 2.4 Pre-Pour Gate |
| 2.3 Embedded Items | → | 2.4 Pre-Pour Gate |
| 2.4 Pre-Pour Gate | → | 2.5 Foundation Concrete |
| 2.5 Foundation Concrete | → | 2.6 Concrete Acceptance |
| 2.6 Concrete Acceptance | → | 3.3 Steel Erection where supported on foundation |
| 2.7 Foundation Walls | → | 2.9 Waterproofing |
| 2.9 Waterproofing | → | 2.10 Insulation |
| 2.9 Waterproofing | → | 2.12 Backfill |
| 2.10 Foundation Insulation | → | 2.12 Backfill |
| 2.11 Foundation Drainage | → | 2.12 Backfill |
| 2.12 Backfill Against Structure | ↔ | 1.6 Backfill |
| 3.2 Steel Materials | → | 3.3 Steel Erection |
| 3.3 Steel Erection | → | 3.4 Bolted Connections |
| 3.3 Steel Erection | → | 3.5 Welding |
| 3.4 Bolted Connections | → | 3.6 Steel Protection |
| 3.5 Welding | → | 3.6 Steel Protection |
| 3.7 Structural Masonry | ↔ | M/E Penetrations |
| 3.7 Structural Masonry | ↔ | Firestopping |
| 3.8 Precast | ↔ | Envelope / M/E / Architectural interfaces |

Three special node types have already emerged

This is important for the eventual data model.

Normal activity: 2.2 Foundation Reinforcement

Gate: 2.4 Pre-Pour Quality Gate

Interface activity: something like 2.3 Embedded Items, which belongs structurally to Substructure but can have relationships with Electrical, Mechanical, Structural, equipment and later commissioning.

So I would give every activity one additional internal property:

nodeType = activity | gate | interface | testing | closeout

We don't need to show that to the field user. It's navigation metadata.

And Build 2 has already justified this distinction: its pre-pour page literally describes itself as a system “even though it sits between modules.”

That is exactly what a gate node is.

Yes. I went back into Build 2 itself for Sections 4–7 and mapped these from the relationships, sequencing, interface checks, pre-concealment gates, examples, and quality gates already established there. I am not replacing the source with a generic construction sequence.

BUILD 3 — MASTER CROSS-LINK MATRIX

Part 2 — Sections 4–7

4. BUILDING ENVELOPE

Build 2 deliberately makes 4.1 Exterior Wall Assemblies an umbrella workflow rather than merely another trade activity. Its objective is coordinating the complete sequence of compatible materials, continuous control layers, drainage/ventilation, openings and interfaces.

It also explicitly defines the critical envelope interface zones as Wall ↔ Foundation, Roof, Window, Door, Structural Steel, Concrete, Mechanical Penetration, Electrical Penetration; Masonry ↔ Flashing; Cladding ↔ Opening; Insulation ↔ Structure; Air Barrier ↔ Opening Membrane; Sealant ↔ Adjacent Materials.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4.1 | Exterior Wall Assemblies | 2.x/3.x structure; approved wall system | 4.2–4.10 | Foundation, Roof, Structural Steel, Concrete, Windows, Doors, M/E | Overall layer sequence, compatibility, continuity, drainage | Envelope testing as specified | Control layers + interfaces before exterior closure |
| 4.2 | Air Barrier | 4.5/substrate accepted as applicable | 4.4, 4.6/4.7, 4.8, 4.9 | 2.9, 5.2, Windows, Doors, M/E penetrations, Structural interfaces | Substrate, product, seams, transitions, openings, penetrations, repairs | Air-barrier/envelope testing where specified | Entire air-control layer before insulation/cladding conceals it |
| 4.3 | Vapour Barrier | Substrate/framing/sheathing as designed | Interior/exterior layers according to designed assembly | 5.2, 6.x, M/E penetrations | Location, continuity, seams, corners, penetrations, repairs | Inspection / envelope testing where applicable | Before drywall/insulation/finish conceals layer |
| 4.4 | Thermal Insulation | Underlying control layer/substrate accepted | 4.6/4.7; interior/exterior closure | Structure, Air Barrier, Windows, Doors, M/E penetrations | Type, thickness, continuity, fastening, gaps, compression, moisture | Thermal/envelope verification where specified | Full insulation condition before cladding/closure |
| 4.5 | Exterior Sheathing | Structural/framing support accepted | 4.2/4.3/4.4 as designed | 3.x, Framing, Openings, M/E | Board type, fastening, joints, flatness, damage | Substrate acceptance | Sheathing fastening/joints before control layers cover it |
| 4.6 | Exterior Masonry / Veneer | Structure/supports; 4.2/4.4 as applicable | 4.10; final envelope acceptance | Structural supports, Air Barrier, Insulation, Windows, Doors, Flashing | Units, mortar, anchors/ties, cavity, flashing, weeps, joints | Masonry testing where specified | Anchors + flashing + cavity + weeps before masonry conceals them |
| 4.7 | Exterior Cladding / Panels | Substrate; 4.2; 4.4; supports accepted | 4.10; final envelope acceptance | Structural, Air Barrier, Insulation, Windows, Doors, Penetrations | Subframing, fasteners, alignment, joints, flashing | System/envelope testing where specified | Air barrier + insulation + subframing/interfaces before panels conceal them |
| 4.8 | Windows / Glazing | Opening accepted; surrounding wall/control layers coordinated | 4.10; envelope testing | 4.1, 4.2, 4.4, 4.6/4.7 | Opening, unit, anchors, shims, flashing, air/water seals, glass | Field water/air testing where specified | Sill/jamb/head flashing + air-barrier transition + insulation before exterior concealment |
| 4.9 | Exterior Doors | Opening/frame support accepted | 4.10; hardware/life-safety; final acceptance | Envelope, Architectural, Fire/Life Safety, Access/Security | Frame, anchors, threshold, weather seals, hardware, operation | Operational / water-air testing where specified | Frame anchorage + perimeter envelope transitions before closure |
| 4.10 | Sealants | Adjacent substrates/components installed and prepared | Envelope final testing/acceptance | 4.6, 4.7, 4.8, 4.9, 5.5, adjacent materials | Compatibility, joint prep, backer rod, primer, dimensions, tooling | Adhesion / envelope testing where specified | Joint preparation/backer rod where no longer observable after sealant |

Build 2 labels 4.2 Air Barrier as one of the highest-priority envelope modules, specifically because failures concentrate at edges, corners, penetrations, openings, transitions and structural interfaces rather than the middle of the membrane.

Likewise, 4.8 Windows/Glazing is explicitly called a high-risk envelope interface and requires integration of anchorage, flashing and air/water sealing into the surrounding wall.

The Build 2 window example gives us a particularly strong composite chain:

Opening → Air Barrier → Sill Membrane → Window → Anchorage → Head/Jamb/Sill Flashing → Perimeter Insulation → Sealant → Testing → Repair/Retest → Closure.

5. ROOFING

Build 2 intentionally separates Roofing from the vertical envelope because of horizontal drainage, ponding, weather exposure, penetrations, curbs, membrane continuity and narrow pre-concealment windows.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5.1 | Roof Deck / Substrate | 3.x roof structure accepted | 5.2 | Structural, M/E openings, Curbs, Drains | Deck, fastening, geometry, slope, openings, surface condition | Survey/substrate acceptance | Deck + openings + curbs + drains before roof layers |
| 5.2 | Vapour / Air Control Layer | 5.1 accepted | 5.3 | 4.2/4.3 wall control layers, Parapets, Curbs, Penetrations, Drains | Product, continuity, seams, penetrations, transitions, repairs | Envelope testing where specified | Entire layer before insulation |
| 5.3 | Roof Insulation | 5.2 accepted | 5.4 | Drains, Curbs, Penetrations, Parapets | Product, thickness, layers, stagger, fastening, taper/slope, dryness | Thickness/slope verification | Insulation before roofing membrane |
| 5.4 | Roofing Membrane | 5.3 accepted | 5.5, 5.6, 5.7, 5.8, 5.9 | Envelope, M/E penetrations, Curbs, Drains | Product, substrate, application, laps, seams, adhesion, fastening | Membrane integrity testing | Membrane before equipment/traffic obscures condition |
| 5.5 | Flashings & Terminations | 5.4; adjacent surfaces/interfaces ready | 5.9 | 4.x wall envelope, Parapets, Edges, Curbs, Penetrations | Laps, terminations, counterflashing, sealants, transitions | Roof/envelope testing | Transitions before caps/cladding/equipment conceal them |
| 5.6 | Roof Penetrations | Coordinated opening/service | 5.9; service completion | 8.9 Mechanical Penetrations; 9.9 Electrical Penetrations; Structural; Envelope | Opening, sleeve/curb, membrane, insulation, air/vapour continuity, flashing | Roof/envelope test where specified | Complete penetration assembly before inaccessible/covered |
| 5.7 | Curbs & Equipment Interfaces | 5.1 structural support; coordinated equipment/curb | Equipment installation; 5.9 | 8.6 HVAC Equipment; Electrical Equipment; Structural; Roofing | Location, dimensions, height, anchorage, insulation, flashing | Equipment/roof acceptance | Curb flashing + roof integration before equipment obscures it |
| 5.8 | Roof Drains | Drain opening + piping coordination + roof assembly | 5.9 | 8.3 Storm Drainage, Roofing, Structure | Location, elevation, sump/taper, membrane clamp, strainer, overflow | Drainage test | Drain-body/roof/piping interface before inaccessible |
| 5.9 | Roofing Testing / Final Inspection | 5.1–5.8 substantially complete | 13.5; 14.x | Envelope, Mechanical, Warranty/Manufacturer | Integrity, drainage, deficiencies, repairs | Water/electronic testing where specified; drainage; retest | Final roof quality gate |

The roofing sequence is unusually clear in Build 2. It defines five gates:

Gate 1: Deck accepted → openings/curbs/drains coordinated
Gate 2: Air/vapour layer accepted before insulation
Gate 3: Insulation accepted before membrane
Gate 4: Membrane/flashings/penetrations/curbs/drains accepted before equipment/traffic obscures them
Gate 5: Testing + drainage + deficiencies + repairs + retesting + warranty documentation.

That means these should become actual gate relationships in the app, not merely hyperlinks.

Roofing Composite Flow

5.1 Deck → GATE → 5.2 Air/Vapour → GATE → 5.3 Insulation → GATE → 5.4 Membrane → 5.5/5.6/5.7/5.8 → GATE → 5.9 Final Roof Acceptance

Build 2 also gives us the rooftop HVAC relationship explicitly:

5.7 Curbs & Equipment Interfaces ↔ 5.6 Roof Penetrations ↔ Mechanical HVAC Equipment, followed eventually by commissioning readiness.

6. INTERIOR ARCHITECTURAL CONSTRUCTION

Build 2 defines the interior mindset as:

Coordination → concealed work → fire continuity → dimensional accuracy → finish readiness → operability.

This section therefore has one of our most important cross-system nodes: wall/ceiling closure.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6.1 | Interior Masonry | Structure/slab accepted; layout | Finishes; doors; M/E completion | Structural, M/E, Fire/Life Safety, Doors | Units, mortar, reinforcement, anchors, openings, geometry | Masonry/grout testing where required | Reinforcement + anchors + M/E + fire/acoustic conditions before grout/concealment |
| 6.2 | Metal Stud Framing | Structure/slab; layout | 6.3, 6.4, 6.5, 6.6 | M/E, Ceilings, Doors, Fire/Life Safety, Finishes | Gauge, spacing, tracks, openings, backing, reinforcement | Dimensional inspection | Framing + backing + rough-ins before board |
| 6.3 | Interior Insulation | 6.2; M/E rough-ins substantially complete | 6.4 | M/E, Fire/Acoustic Assemblies | Type, thickness, continuity, services, compression, moisture | Inspection | Entire insulation installation before board |
| 6.4 | Gypsum Board | Interior Pre-Concealment Gate released | 7.3, 7.4, final architectural | 6.2, 6.3, 6.5, M/E, Firestopping | Type, layers, orientation, fasteners, joints, perimeters | Assembly inspection | First-side/second-side closure gates as applicable |
| 6.5 | Fire-Rated Assemblies | Approved listed assembly; framing/masonry | Closure; 10.x Fire/Life Safety | 10.1, 10.2, 10.3, M/E penetrations, Doors, Dampers | Rating, components, continuity, joints, openings, penetrations | Fire/life-safety acceptance where required | Critical fire-rated pre-concealment gate |
| 6.6 | Interior Doors & Frames | Wall/opening/framing ready | 6.7, 7.x, 10.5 | Walls, Hardware, Access Control, Fire/Life Safety, Finishes | Frame, anchoring, handing, alignment, clearances | Operational inspection | Frame anchorage/reinforcement before wall closure where concealed |
| 6.7 | Door Hardware | 6.6; finishes sufficiently complete | 7.7; 10.5; turnover | Fire/Life Safety, Security/Access Control, Electrical | Hardware set, closer, latch, lock, panic device, seals | Operation/function testing | Concealed electrified hardware/wiring where applicable |
| 6.8 | Ceilings | Above-ceiling work ready; support/layout | 7.7 / turnover | HVAC, Electrical, Fire Alarm, Sprinklers, Access Panels | Grid, suspension, elevation, panels, devices, access | Ceiling inspection | Major above-ceiling pre-concealment gate |
| 6.9 | Access Panels | Maintainable item/location established | Ceiling/wall completion; turnover | Mechanical, Electrical, Controls, Fire/Life Safety | Size, location, rating, anchoring, operation | Maintainability/access verification | Confirm access requirement before wall/ceiling closure |

Build 2 explicitly says that access panels exist wherever concealed equipment, valves, dampers, controls or other maintainable components require future access.

And it gives us the master pre-concealment gate directly. Before a wall or ceiling closes, the system checks current wall/ceiling and MEP/fire documents, framing/masonry, openings, backing, reinforcement, anchors/supports, rough-ins, tests, boxes/sleeves, support and unresolved clashes.

So we need a special virtual gate:

G-INT-01 — Wall / Ceiling Pre-Concealment Gate

Inputs:

6.1 / 6.2 + 6.3 + M/E Rough-ins + 6.5/10.x Fire Integrity + 6.9 Access + Tests + Deficiency Status

↓

G-INT-01

↓

Release 6.4 Gypsum / 6.8 Ceiling Closure

This may become one of the most useful buttons in the whole application.

Build 2's rated-wall example proves the chain:

Metal Stud Framing → MEP Rough-In → Interior Insulation → Fire Integrity/Firestop → Evidence → Wall Closure.

7. FINISHES

Build 2 deliberately shifts the quality logic here toward:

substrate readiness → environmental conditions → approved material/system → installation → workmanship → visual uniformity → protection → final deficiency closure.

| ID | Activity | Before / Prerequisites | After / Downstream | Interfaces | Related QC | Testing / Acceptance | Pre-Concealment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7.1 | Concrete Floor Preparation | 2.8 Slab-on-Grade / structural slab accepted | 7.2 | Drains, Penetrations, Equipment Bases, M/E | Moisture, cracks, contamination, profile, flatness/levelness, repairs | Moisture/profile testing as specified | Substrate condition before finish covers it |
| 7.2 | Floor Finishes | 7.1 accepted | 7.7 | Architectural, Equipment, Doors, Drains | Tile / resilient / epoxy systems; layout; adhesion; joints; cure | Adhesion/thickness/moisture etc. per system | Substrate/primer/membrane layers where concealed |
| 7.3 | Wall Finishes | 6.1/6.4 substrate accepted | 7.7 | Doors, M/E devices, Sealants, Specialty finishes | Substrate, material, layout, joints, penetrations, appearance | Finish-specific testing | Hidden backing/adhesive/membranes as applicable |
| 7.4 | Painting / Coatings | Substrate/gypsum/masonry/steel accepted | 7.7 | Architectural, Structural Steel Protection where relevant, M/E | Surface prep, approved system, environment, application, thickness, cure | DFT/adhesion etc. where specified | Surface preparation/primer before subsequent coats |
| 7.5 | Architectural Sealants | Adjacent finished substrates prepared | 7.7 | Walls, Floors, Doors, Sanitary Interfaces, Acoustic Assemblies | Compatibility, joint prep, backing, primer, application, tooling | Adhesion where specified | Backer/joint preparation before sealant |
| 7.6 | Specialty Finishes | Approved substrate/system | 7.7 | Architectural, M/E, Equipment | Product-specific installation, attachment, joints, finish | Manufacturer/system-specific testing | Depends on specialty system |
| 7.7 | Final Architectural Deficiency Inspection | 6.x + 7.1–7.6 substantially complete | 14.x Deficiency/Closeout | All Architectural + M/E visible interfaces | Identification, documentation, assignment, correction, reinspection | Final acceptance/reinspection | — |

Build 2 explicitly calls 7.7 the point where all interior architectural quality streams converge and defines its purpose as identifying, documenting, assigning, verifying and closing deficiencies before turnover.

So 7.7 is not just another activity node.

It should be:

nodeType = closeoutHub

and eventually link directly to Section 14.

The finishes master gate also explicitly requires acceptable substrates, approved/undamaged materials, correct installation/layout/thickness/joints/appearance, appropriate environmental conditions and respected cure times.

MASTER CROSS-LINKS — SECTIONS 4–7

These are the significant graph edges we now establish.

| From | Relationship | To |
| --- | --- | --- |
| 2.7 Foundation Walls | → | 4.1 Exterior Wall Assemblies |
| 2.9 Below-Grade Waterproofing | ↔ | 4.2 Air Barrier / envelope transition |
| 3.x Superstructure | → | 4.1 Exterior Wall Assemblies |
| 3.3 Structural Steel | ↔ | 4.1 Exterior Wall Assemblies |
| 4.1 Exterior Wall Assemblies | hub | 4.2–4.10 |
| 4.2 Air Barrier | ↔ | 5.2 Roof Air/Vapour Control |
| 4.2 Air Barrier | ↔ | 4.8 Windows |
| 4.2 Air Barrier | ↔ | 4.9 Exterior Doors |
| 4.2 Air Barrier | ↔ | 5.5 Roof Flashing/Terminations |
| 4.2 Air Barrier | ↔ | 5.6 Roof Penetrations |
| 4.2 Air Barrier | ↔ | Mechanical/Electrical penetrations |
| 4.3 Vapour Barrier | ↔ | 5.2 Roof Air/Vapour Control |
| 4.3 Vapour Barrier | ↔ | M/E penetrations |
| 4.4 Thermal Insulation | ↔ | 4.8 Windows |
| 4.4 Thermal Insulation | ↔ | 4.9 Doors |
| 4.4 Thermal Insulation | ↔ | 5.3 Roof Insulation |
| 4.6 Masonry/Veneer | ↔ | 4.8 Windows |
| 4.6 Masonry/Veneer | ↔ | 4.9 Doors |
| 4.6 Masonry/Veneer | ↔ | 4.10 Sealants |
| 4.7 Cladding | ↔ | 4.8 Windows |
| 4.7 Cladding | ↔ | 4.9 Doors |
| 4.7 Cladding | ↔ | 4.10 Sealants |
| 4.8 Windows | → | 4.10 Sealants |
| 4.8 Windows | → | 13.5 Envelope Testing |
| 4.9 Exterior Doors | ↔ | Fire/Life Safety |
| 4.9 Exterior Doors | → | 4.10 Sealants |
| 5.1 Roof Deck | → | 5.2 Air/Vapour Layer |
| 5.2 Air/Vapour | → | 5.3 Insulation |
| 5.3 Insulation | → | 5.4 Membrane |
| 5.4 Membrane | ↔ | 5.5 Flashings |
| 5.4 Membrane | ↔ | 5.6 Penetrations |
| 5.4 Membrane | ↔ | 5.7 Curbs |
| 5.4 Membrane | ↔ | 5.8 Drains |
| 5.6 Roof Penetrations | ↔ | Mechanical Penetrations |
| 5.6 Roof Penetrations | ↔ | Electrical Penetrations |
| 5.7 Curbs | ↔ | HVAC Equipment |
| 5.7 Curbs | ↔ | Structural Supports |
| 5.8 Roof Drains | ↔ | Storm Drainage |
| 5.1–5.8 | → | 5.9 Roofing Final Gate |
| 5.9 Roofing Final Inspection | → | 13.5 Envelope Testing |
| 6.1 Interior Masonry | ↔ | Fire-Rated Assemblies |
| 6.1 Interior Masonry | ↔ | M/E Penetrations |
| 6.2 Stud Framing | → | 6.3 Interior Insulation |
| 6.2 Stud Framing | ↔ | 6.6 Door Frames |
| 6.2 Stud Framing | ↔ | M/E Rough-In |
| 6.3 Interior Insulation | → | G-INT-01 |
| 6.5 Fire-Rated Assemblies | → | G-INT-01 |
| M/E Rough-In | → | G-INT-01 |
| Firestopping | → | G-INT-01 |
| Access Requirements | → | G-INT-01 |
| G-INT-01 | → | 6.4 Gypsum Closure |
| G-INT-01 | → | 6.8 Ceiling Closure |
| 6.5 Fire-Rated Assemblies | ↔ | 10.1/10.2 Rated Construction |
| 6.5 Fire-Rated Assemblies | ↔ | 10.3 Firestopping |
| 6.6 Interior Doors | → | 6.7 Hardware |
| 6.6 Interior Doors | ↔ | 10.5 Fire-Rated Doors |
| 6.7 Hardware | ↔ | Access Control / Electrical |
| 6.7 Hardware | ↔ | 10.5 Fire-Rated Doors |
| 6.8 Ceilings | ↔ | HVAC Devices |
| 6.8 Ceilings | ↔ | Lighting |
| 6.8 Ceilings | ↔ | Fire Alarm |
| 6.8 Ceilings | ↔ | Fire Protection |
| 6.8 Ceilings | ↔ | 6.9 Access Panels |
| 6.9 Access Panels | ↔ | Valves / Dampers / Controls / Electrical access |
| 2.8 Slab-on-Grade | → | 7.1 Concrete Floor Preparation |
| 7.1 Concrete Floor Preparation | → | 7.2 Floor Finishes |
| 6.1/6.4 | → | 7.3 Wall Finishes |
| 6.4 Gypsum | → | 7.4 Painting/Coatings |
| 7.2–7.6 | → | 7.7 Final Architectural Deficiency Inspection |
| 7.7 | → | 14.x Deficiency / Completion / Closeout |

We now have three more special navigation objects

After Sections 1–7, our node taxonomy is becoming clearer:

activity — normal construction/QC activity
umbrella — coordinates several component activities
gate — work cannot logically progress until conditions are satisfied
interface — exists primarily because systems intersect
testing — acceptance/testing node
closeoutHub — convergence toward completion/turnover

Examples:

- 4.1 Exterior Wall Assemblies = umbrella

- 4.8 Windows = interface-heavy activity

- 5.9 Roofing Testing/Final Inspection = gate + testing

- G-INT-01 Wall/Ceiling Pre-Concealment = gate

- 6.9 Access Panels = interface

- 7.7 Final Architectural Deficiency Inspection = closeoutHub

We should allow more than one tag per node rather than forcing every node into exactly one category.

That will make the eventual app considerably smarter.

For example, tapping “Before Concealment” would not merely search text. It could filter the graph for nodes tagged gate and surface:

Bottom of Excavation → Foundation Pre-Pour → Waterproofing Before Backfill → Air Barrier → Roof Control Layer → Roof Insulation → Roof Final Membrane → Wall Closure → Ceiling Closure...

That is exactly the sort of navigation intelligence we wanted Build 3 to establish.

Sections 1–7 are now mapped. The next block—8 Mechanical + 9 Electrical + 10 Fire/Life Safety—is where this becomes a genuine multidisciplinary field-quality graph, because almost everything there connects backward into the structural, envelope, roofing and architectural nodes we have just established.

Yes. 8, 9 and 10 now, again grounded in Build 2 and continuing the Build 3 cross-link architecture.

These three sections are especially important because Build 2 itself says the system should stop behaving like isolated checklists: architectural closure can depend on mechanical testing, electrical concealed work, firestopping, dampers, insulation and deficiencies.

BUILD 3 — MASTER CROSS-LINK MATRIX

Part 3 — Sections 8–10

8. MECHANICAL SERVICES

Build 2 defines the universal mechanical workflow as:

Approved system → routing/layout → material/equipment verification → installation → supports → penetrations → testing → insulation → identification → commissioning interface → closure.

It also explicitly limits the inspector's technical authority: installation quality, conformity, documentation and evidence can be controlled, while specialized calculations, balancing, equipment-performance interpretation and design judgments must follow approved documents and the appropriate mechanical professional/Responsable qualité.

| ID | Activity | Before / Prerequisites | After / Downstream | Major Interfaces | Testing / Acceptance | Critical Gate |
| --- | --- | --- | --- | --- | --- | --- |
| 8.1 | Plumbing — Domestic Water | Structure/openings; approved routing/materials | 8.7, 8.10, 8.11 | Structure, Walls/Ceilings, 8.9, Equipment | Pressure/leak/flush etc. as required | Test before insulation/concealment |
| 8.2 | Sanitary Drainage | Structure/openings; approved routing | 8.7, 8.10, 8.11 | Slabs, Walls, Fixtures, 8.9 | Drainage/leak testing as required | Slope/joints/connections/test before concealment |
| 8.3 | Storm Drainage | Roof/site drainage coordination | 8.7, 8.10, 8.11 | 5.8 Roof Drains, Site Drainage, 8.9 | Drainage/leak test | Roof drain + leader + horizontal system before closure |
| 8.4 | Process / Equipment Piping | Equipment/system design established | 8.7, 8.10, 8.11 | 8.6, Structure, Electrical/Controls | Pressure/flush/clean as applicable | Test before insulation |
| 8.5 | HVAC Ductwork | Routing/coordination/supports established | 8.7, 8.8, 8.10 | 6.8 Ceilings, 10.4 Dampers, 8.6 Equipment, 8.9 | Leakage/TAB/functional evidence as applicable | Duct/support/damper/access before ceiling closure |
| 8.6 | HVAC Equipment | Bases/curbs/supports ready | 8.8, 8.10, commissioning | 5.7 Curbs, Electrical, Controls, Ductwork, Piping, Drains | Manufacturer start-up / functional testing | Equipment-interface readiness |
| 8.7 | Mechanical Insulation | Mechanical installation + required testing accepted | Concealment / final mechanical completion | Piping, Ductwork, Equipment, Penetrations | Inspection of continuity/vapour protection | Never insulate over unresolved/test-unaccepted work |
| 8.8 | Mechanical Controls / BAS Interfaces | Equipment/devices installed | Commissioning / 13.x | 8.6 Equipment, 9.x Electrical, Controls/BAS | Functional commissioning | Physical installation ≠ controls acceptance |
| 8.9 | Mechanical Penetrations | Opening/service coordinated | Closure of wall/floor/roof | Structure, 4.x Envelope, 5.6 Roof, 6.x Interior, 10.3 Firestop | Fire/envelope/finish acceptance as applicable | Major multidisciplinary pre-concealment interface |
| 8.10 | Mechanical Testing | Relevant installation complete enough to test | 8.7 / commissioning / closure | All mechanical systems | Pressure, flushing, cleaning, balancing etc. per approved requirements | FAIL → correct → reinspect → RETEST |
| 8.11 | Mechanical Identification | Installed system/equipment IDs finalized | Commissioning / O&M / turnover | BAS, O&M, Equipment | Identification verification | Required for commissioning/operations readiness |

Build 2 specifically makes 8.9 Mechanical Penetrations a major multidisciplinary interface, requiring restoration of structural, fire, air, water, acoustic and finish performance.

And 8.10 is explicitly traceability-heavy: testing, flushing, cleaning and balancing demonstrate that the systems are intact, clean, functional and ready for commissioning.

Mechanical master chain

8.1–8.6 Installation

↓

8.9 Penetration/Interface Control

↓

8.10 Required Testing

↓

PASS?

NO → Deficiency/NC → Correct → Reinspect → Retest

YES ↓

8.7 Insulation where applicable

↓

8.8 Controls/BAS

↓

8.11 Identification

↓

13.x Commissioning / Acceptance

The crucial dependency here is:

Installation does not automatically authorize insulation or concealment.

For systems where Build 2 requires testing first:

Installed → Inspected → Tested/Accepted → Insulated → Concealed

not

Installed → Insulated → "we'll test it later."

9. ELECTRICAL BUILDING SERVICES

Build 2 puts an even stronger authority boundary around this section because Hochelaga is an electrical-substation project. The inspector controls building-quality execution, approved materials, physical installation, interfaces, traceability, test evidence and closure, but specialized electrical acceptance, energization, protection, cable testing, grounding performance and design interpretation belong to the applicable PIE/PRIE and authorized electrical specialists.

The Build 2 electrical flow is:

Approved documents/materials → routing/layout → physical installation → supports → penetrations/interfaces → equipment installation → grounding/bonding interfaces → identification → testing evidence → deficiency correction → verification → closure.

| ID | Activity | Before / Prerequisites | After / Downstream | Major Interfaces | Testing / Acceptance | Critical Gate |
| --- | --- | --- | --- | --- | --- | --- |
| 9.1 | Conduits / Raceways | Current electrical/coordination drawings | Cable work/equipment connections | Concrete, Rebar, Walls, Ceilings, 9.9 | Raceway readiness / specialist verification as required | Embedded/concealed conduit inspection before pour/closure |
| 9.2 | Cable Trays | Structure/support route coordinated | Cable installation | 9.3, Structure, Mechanical, Firestop, Access | Bonding/specialist verification as required | Route/support/clearance/penetrations before cable loading |
| 9.3 | Supports / Hangers | Structure + approved support details | 9.1, 9.2, 9.4 | 3.x Structure, Mechanical, Ceilings | Physical inspection | Support accepted before system loading/concealment |
| 9.4 | Electrical Equipment Installation | Base/room/environment ready | 9.5, 9.6, 9.10, 9.11 | Structure, Architectural, Mechanical, Controls | Specialist testing/acceptance | Physical installation ≠ electrical technical acceptance |
| 9.5 | Building Distribution Interfaces | Distribution equipment/routes established | 9.11 / commissioning | Mechanical Equipment, Controls, Emergency Systems, Panels | Specialist acceptance | Interface-control node |
| 9.6 | Grounding / Bonding | Structural/equipment installation coordinated | 9.11 | Concrete, Structural Steel, Equipment, Raceways/Trays | Authorized specialist test | Concealed grounding evidence before concrete/closure |
| 9.7 | Lighting | Ceiling/layout/support ready | Functional completion | 6.8 Ceiling, Controls, 9.8 | Functional evidence | Above-ceiling/support interface before closure |
| 9.8 | Emergency Lighting | Life-safety/electrical arrangement established | 10.7 / final life-safety acceptance | Emergency Power, Exit Signage, Fire/Life Safety | Functional test | Specialist functional acceptance |
| 9.9 | Electrical Penetrations | Opening/service coordinated | Wall/floor/roof closure | Structure, 4.x Envelope, 5.6 Roof, 6.x Interior, 10.3 Firestop | Fire/envelope restoration | Major multidisciplinary gate |
| 9.10 | Identification / Labels | Final equipment/circuit/system naming established | 9.11 / turnover | Panels, Equipment, O&M, Controls | Identification verification | Must correspond to drawings/schedules/O&M |
| 9.11 | Electrical Testing Interfaces | Construction sufficiently complete | Energization / commissioning / turnover | 13.x Testing & Commissioning | Authorized specialist testing | Test evidence + failure/retest + acceptance |

9.1 is a particularly important cross-link

Build 2 asks:

Will this conduit still be inspectable once concrete, drywall or ceiling closure happens?

If not, inspection and evidence capture must happen first.

That gives us several direct dependencies:

9.1 Embedded Conduit → Concrete Pre-Pour Gate

9.1 Concealed Conduit → G-INT-01 Wall/Ceiling Closure Gate

9.1 Penetration → 9.9 Electrical Penetration

Build 2 even gives the embedded-conduit failure scenario: a displaced equipment stub-up discovered before the pour leads to local pour control, repositioning, securing, remeasurement, photography, reinforcement/interface re-verification and only then closure before concrete.

So 9.1 is not downstream of structure only.

Sometimes electrical becomes a prerequisite to structural closure.

9.9 — Electrical Penetrations

This should be treated similarly to 8.9 but linked to the electrical service.

Build 2 itself calls it one of the most important building-quality electrical interfaces, requiring structural coordination plus restoration of fire, air, water and acoustic control.

Therefore:

9.9 ↔ 3.x Structure
9.9 ↔ 4.2 Air Barrier
9.9 ↔ 4.3 Vapour Barrier
9.9 ↔ 5.6 Roof Penetrations
9.9 ↔ 6.5 Fire-Rated Assemblies
9.9 ↔ 10.3 Firestopping
9.9 → G-INT-01

And Build 2's closure criteria explicitly require:

penetration approved + structure accepted + sleeve/opening accepted + firestop complete + air/water seal complete + finish complete + evidence filed.

That makes 9.9 a genuine interface + gate node.

10. FIRE & LIFE-SAFETY CONSTRUCTION

Build 2 defines this entire section around preservation of:

fire resistance + smoke control + compartmentation + egress + fire protection.

The workflow is:

Identify rated condition → establish approved assembly/system → verify materials → inspect progressively → control penetrations/interfaces → inspect before concealment → document → deficiency/NC → correct → reinspect → specialist testing/acceptance where required → close.

| ID | Activity | Before / Prerequisites | After / Downstream | Major Interfaces | Testing / Acceptance | Critical Gate |
| --- | --- | --- | --- | --- | --- | --- |
| 10.1 | Fire-Rated Walls | Approved rated assembly; framing/masonry | Wall closure / final life safety | 6.1–6.5, 8.9, 9.9, 10.3, 10.5 | Assembly inspection | Before wall closure |
| 10.2 | Fire-Rated Floors / Ceilings | Approved horizontal assembly | Ceiling/floor closure | Structure, 6.8, M/E, 10.3, Dampers | Assembly inspection | Before horizontal assembly is concealed |
| 10.3 | Firestopping | Penetration/opening + rated assembly identified | Wall/floor/ceiling closure | 8.9 + 9.9 + 10.1 + 10.2 + all penetrating services | Listed-system verification / specialist acceptance where required | HIGH-CONTROL PRE-CONCEALMENT NODE |
| 10.4 | Fire / Smoke Dampers | Rated opening + ductwork coordinated | Ceiling/wall closure | 8.5 HVAC Ductwork, 8.8 Controls, 10.1/10.2, 6.9 Access | Functional inspection/testing | Damper + access + fire interface before closure |
| 10.5 | Fire-Rated Doors | Rated opening/wall + correct door/frame | 10.7 / final life safety | 6.6 Doors, 6.7 Hardware, 10.1, Access Control | Closing/latching/function verification | Complete assembly acceptance |
| 10.6 | Fire-Alarm Physical Installation Interfaces | Electrical rough-in/devices + architectural conditions | 10.7 / commissioning | 9.x Electrical, 6.8 Ceiling, 8.x Mechanical, 10.4 Dampers | Authorized fire-alarm specialist testing | Physical QC separated from technical system acceptance |
| 10.7 | Emergency / Life-Safety Interfaces | Component systems substantially complete | Final integrated acceptance | 9.8 Emergency Lighting, 10.5 Doors, 10.6 Alarm, Mechanical, Emergency Power, Egress | Functional/integrated testing | Life-safety convergence hub |
| 10.8 | Fire Protection Systems | Approved system + supports/routes/openings | 10.7 / commissioning | Structure, Ceilings, Fire Alarm, Water Supply, 10.3 | Specialist testing/acceptance | System acceptance before turnover |

10.3 FIRESTOPPING — SPECIAL STATUS

This needs a stronger node classification than almost anything we've done so far.

Build 2 itself says:

“This should be one of the most rigorous modules in the entire application.”

And explains that firestop is an approved system, not merely sealant around a penetration: assembly + opening + penetrating item + annular space + backing/fill + firestop material + required depth/configuration + installation conditions.

Therefore:

10.3 = highControl + interface + gate + traceabilityCritical

Every penetration through rated construction should potentially create a Firestop Instance.

For example:

FS-024

Rated Wall W2H → 2-hour assembly → 50 mm conduit → approved system X → installer → inspection → photo → deficiency? → correction → reinspection → CLOSED

And crucially:

A later penetration must reopen the quality status.

Build 2 already establishes exactly this logic: if an electrician later adds a conduit through an accepted wall, the rated assembly has been modified, so the new penetration must be identified, matched to an approved firestop system, inspected, photographed and added to the penetration register before the wall's quality status is restored.

That means our graph needs state invalidation.

That is important.

An accepted node does not necessarily stay accepted forever if downstream work physically modifies it.

10.4 FIRE/SMOKE DAMPERS

This becomes a beautiful example of why Build 3 exists.

A damper isn't simply "mechanical."

Build 2 requires the correct approved damper, correct location/orientation, interfaces, access and functional inspection/testing evidence.

Its graph looks more like:

10.1 Rated Wall / 10.2 Rated Assembly

↕
8.5 Ductwork

↕
10.4 Fire/Smoke Damper

↕
8.8 Controls/BAS

↕
10.6 Fire Alarm

↕
6.9 Access Panel

↓

Functional Test

↓

10.7 Life-Safety Acceptance

Now we are no longer thinking in "trades."

We're thinking in systems.

10.5 FIRE-RATED DOORS

Build 2 defines the rated door as the entire compatible assembly:

door + frame + glazing + hardware + surrounding wall interface + correct operation.

So:

6.5 Rated Assembly
↓
6.6 Door/Frame
↓
6.7 Hardware
↓
10.5 Fire-Rated Door Assembly
↓
Closing/Latching/Functional Verification
↓
10.7 Life-Safety

Again, 10.5 is therefore an assembly/interface node, not merely a duplicate of 6.6.

10.6 FIRE ALARM

Build 2 makes the authority split very clean here:

The QC role verifies physical installation, location, identification, accessibility and building interfaces, while programming, circuit performance and acceptance testing remain with authorized personnel.

So we should separate:

Physical QC

from

Technical Acceptance

in the app.

For example:

FA-DET-024

Physical status: ✅ Accepted
Electrical completion: ✅
Programming: ⏳
Functional test: ⏳
Integrated test: ⏳
Overall status: 🟡 NOT YET ACCEPTED

That distinction will prevent a dangerous logical error:

Installed ≠ commissioned ≠ accepted.

10.7 — LIFE-SAFETY CONVERGENCE HUB

This is one of our major Build 3 hubs.

Build 2 explicitly says 10.7 connects several systems rather than representing one trade, namely emergency lighting, exit signage, fire alarm, doors, mechanical systems, emergency power and egress construction.

Therefore:

10.7 = interfaceHub + testingHub + acceptanceGate

Inputs can include:

9.8 Emergency Lighting
10.5 Fire-Rated Doors
10.6 Fire Alarm
10.4 Fire/Smoke Dampers
10.8 Fire Protection
9.5 Emergency Electrical Interfaces
Architectural Egress Conditions

↓

G-LS-01 — LIFE-SAFETY INTEGRATED READINESS

↓

Functional / integrated testing

↓

Failures?

YES → assign system → correct → reinspect → retest

NO ↓

LIFE-SAFETY ACCEPTED

MASTER CROSS-LINKS — SECTIONS 8–10

| From | Relationship | To |
| --- | --- | --- |
| 8.1 Domestic Water | → | 8.10 Mechanical Testing |
| 8.1 Domestic Water | → | 8.7 Mechanical Insulation |
| 8.2 Sanitary | → | 8.10 Mechanical Testing |
| 5.8 Roof Drains | ↔ | 8.3 Storm Drainage |
| 8.3 Storm Drainage | ↔ | Site Drainage |
| 8.4 Process Piping | ↔ | 8.6 Equipment |
| 8.4 Process Piping | → | 8.10 Testing |
| 8.5 Ductwork | ↔ | 8.6 HVAC Equipment |
| 8.5 Ductwork | ↔ | 10.4 Fire/Smoke Dampers |
| 8.5 Ductwork | ↔ | 6.8 Ceilings |
| 8.6 HVAC Equipment | ↔ | 5.7 Roof Curbs |
| 8.6 HVAC Equipment | ↔ | 9.5 Electrical Distribution Interfaces |
| 8.6 HVAC Equipment | ↔ | 8.8 Controls/BAS |
| 8.6 HVAC Equipment | → | 8.10 Testing |
| 8.10 Mechanical Testing | → | 8.7 Mechanical Insulation where test must precede insulation |
| 8.8 BAS | ↔ | 9.x Electrical |
| 8.8 BAS | ↔ | 10.4 Dampers |
| 8.9 Mechanical Penetrations | ↔ | Structure |
| 8.9 | ↔ | 4.x Envelope |
| 8.9 | ↔ | 5.6 Roof Penetrations |
| 8.9 | ↔ | 6.x Interior Construction |
| 8.9 | ↔ | 10.3 Firestopping |
| 8.9 | → | G-INT-01 |
| 8.10 Mechanical Testing | → | 13.x Testing/Commissioning |
| 8.11 Identification | → | Commissioning/O&M |
| 9.1 Embedded Conduits | → | Concrete Pre-Pour Gate |
| 9.1 Concealed Raceways | → | G-INT-01 |
| 9.1 | ↔ | 9.9 Penetrations |
| 9.2 Cable Trays | ↔ | 9.3 Supports |
| 9.2 | ↔ | 9.9 Penetrations |
| 9.3 Supports | ↔ | Structure |
| 9.4 Electrical Equipment | ↔ | Structure/Equipment Bases |
| 9.4 | ↔ | 9.5 Distribution |
| 9.4 | ↔ | 9.6 Grounding |
| 9.4 | → | 9.11 Testing |
| 9.5 Distribution Interfaces | ↔ | 8.6 Mechanical Equipment |
| 9.5 | ↔ | 8.8 Controls |
| 9.5 | ↔ | Emergency Systems |
| 9.6 Grounding/Bonding | ↔ | Concrete / Structural Steel |
| 9.6 | → | 9.11 Specialist Testing |
| 9.7 Lighting | ↔ | 6.8 Ceilings |
| 9.8 Emergency Lighting | → | 10.7 Life-Safety Interfaces |
| 9.9 Electrical Penetrations | ↔ | Structure |
| 9.9 | ↔ | 4.x Envelope |
| 9.9 | ↔ | 5.6 Roof Penetrations |
| 9.9 | ↔ | 6.x Interiors |
| 9.9 | ↔ | 10.3 Firestopping |
| 9.9 | → | G-INT-01 |
| 9.10 Identification | → | 9.11 / O&M |
| 9.11 Electrical Testing | → | 13.x Commissioning |
| 10.1 Rated Walls | ↔ | 6.5 Fire-Rated Assemblies |
| 10.1 | ↔ | 8.9 Mechanical Penetrations |
| 10.1 | ↔ | 9.9 Electrical Penetrations |
| 10.1 | ↔ | 10.3 Firestopping |
| 10.1 | ↔ | 10.5 Fire Doors |
| 10.2 Rated Floors/Ceilings | ↔ | Structure |
| 10.2 | ↔ | 6.8 Ceilings |
| 10.2 | ↔ | 10.3 Firestopping |
| 10.2 | ↔ | 10.4 Dampers |
| 10.3 Firestopping | → | G-INT-01 Wall/Ceiling Closure |
| 10.3 | ↔ | 8.9 Mechanical Penetrations |
| 10.3 | ↔ | 9.9 Electrical Penetrations |
| 10.4 Dampers | ↔ | 8.5 Ductwork |
| 10.4 | ↔ | 8.8 BAS |
| 10.4 | ↔ | 10.6 Fire Alarm |
| 10.4 | ↔ | 6.9 Access Panels |
| 10.4 | → | 10.7 Life Safety |
| 10.5 Fire Doors | ↔ | 6.6 Doors & Frames |
| 10.5 | ↔ | 6.7 Hardware |
| 10.5 | → | 10.7 Life Safety |
| 10.6 Fire Alarm | ↔ | 9.x Electrical |
| 10.6 | ↔ | 6.8 Ceilings |
| 10.6 | ↔ | 10.4 Dampers |
| 10.6 | → | 10.7 Life Safety |
| 10.8 Fire Protection | ↔ | Structure / Ceiling / Water / Alarm |
| 10.8 | ↔ | 10.3 Firestopping |
| 10.8 | → | 10.7 Life-Safety Acceptance |
| 10.7 Life Safety | → | 13.x Integrated Testing / Acceptance |

THREE MAJOR CROSS-SYSTEM GATES NOW EMERGE

G-MEP-01 — MEP PRE-CONCEALMENT

Before drywall/ceiling closure:

Mechanical rough-in accepted

- Mechanical required tests passed

- Electrical rough-in accepted

- Concealed electrical documented

- Mechanical/electrical penetrations accepted

- Firestop accepted

- Dampers accepted

- Insulation complete where required

- Required access preserved

- Open deficiencies controlled

↓

RELEASE WALL / CEILING CLOSURE

This directly implements Build 2's statement that ceiling closure can depend on mechanical testing, electrical concealed work, firestopping, dampers, insulation and deficiencies.

G-MEP-02 — EQUIPMENT COMMISSIONING READINESS

Equipment physically installed

- Supports/anchors

- Piping

- Ductwork

- Drains

- Electrical

- Grounding/bonding interface

- Controls

- Identification

- Required preliminary tests

- Deficiencies controlled

↓

READY FOR START-UP / COMMISSIONING

G-LS-01 — LIFE-SAFETY INTEGRATED READINESS

Rated construction accepted

- Firestopping accepted

- Dampers accepted

- Fire doors accepted

- Emergency lighting accepted

- Fire alarm physical installation accepted

- Fire protection installation accepted

- Emergency interfaces complete

↓

READY FOR INTEGRATED LIFE-SAFETY TESTING

↓

PASS → LIFE-SAFETY ACCEPTED

And this block establishes an important architectural rule for the application:

A node can be complete locally while the system containing it remains incomplete globally.

A duct can be installed, but the ceiling cannot close.
A fire-alarm detector can be physically accepted, but the fire-alarm system is not accepted.
An AHU can be installed, but it is not commissioning-ready.
A rated wall can be accepted, then lose that accepted state when someone makes a new penetration through it.

That is precisely the difference between the Build 2 checklists and the Build 3 decision graph we are constructing.

Sections 1–10 are now mapped.

Exactly. 11, 12, 13 and 14 are the remaining Build 3 mapping, and in some ways they matter even more than 1–10 because they are the sections that connect, prove and close everything upstream.

Build 2 itself ends by saying the next step is to convert the field content into an app/QMS with common templates, inspection gates, status logic, cross-references and daily workflows.

BUILD 3 — MASTER CROSS-LINK MATRIX

Part 4 — Sections 11–14

11. MULTIDISCIPLINARY INTERFACES

This is effectively the cross-linking engine of the whole framework.

Build 2 defines the workflow as:

Identify interface → identify affected disciplines → establish governing documents → coordinate sequence → inspect prerequisites → inspect physical interface → verify concealed conditions → document → resolve conflicts → verify correction → close interface.

| ID | Interface | Primary Links | Upstream / Prerequisites | Downstream / Gate |
| --- | --- | --- | --- | --- |
| 11.1 | Structural ↔ Architectural | 3.x ↔ 4.x/5.x/6.x/7.x | Structural geometry/support/openings | Architectural installation/closure |
| 11.2 | Structural ↔ Mechanical | 3.x ↔ 8.x | Openings, embeds, bases, supports | Mechanical installation/testing |
| 11.3 | Structural ↔ Electrical | 3.x ↔ 9.x | Embedded conduits, grounding, openings, supports | Pour/closure/electrical completion |
| 11.4 | Envelope ↔ Mechanical | 4.x/5.x ↔ 8.x | Opening/curb/penetration | Air/water/thermal restoration |
| 11.5 | Envelope ↔ Electrical | 4.x/5.x ↔ 9.x | Opening/penetration | Air/water/thermal restoration |
| 11.6 | Architectural ↔ MEP | 6.x/7.x ↔ 8.x/9.x/10.x | Rough-ins/above-ceiling work | Wall/ceiling/finish closure |
| 11.7 | Universal Penetrations | 3.x + 4.x + 5.x + 6.x + 8.9 + 9.9 + 10.3 | Approved opening/service | Complete restored assembly |
| 11.8 | Embedded Items | 3.x + 8.x + 9.x | Coordination before concrete | Concrete pre-pour release |
| 11.9 | Equipment Bases / Pads | 3.x + 8.6 + 9.4 | Equipment data/layout | Equipment installation |
| 11.10 | Access & Maintainability | 6.x + 8.x + 9.x + 10.x | Final spatial configuration | Completion/commissioning |
| 11.11 | Trade Coordination / Congestion | ALL relevant disciplines | Coordinated routing/layout | Installation/closure |

Build 2 specifically elevates 11.7, 11.10 and 11.11 because penetrations occur across disciplines, equipment can be technically installed yet impossible to maintain, and congestion can generate field conflicts/rework.

11.7 — UNIVERSAL PENETRATION HUB

This should not duplicate 8.9 or 9.9.

Instead:

11.7 = universal parent/interface workflow

with:

8.9 Mechanical Penetration
9.9 Electrical Penetration
10.3 Firestop
5.6 Roof Penetration
Structure
Envelope
Architectural Finish

feeding it.

Universal penetration lifecycle

Opening

→ Sleeve

→ Service

→ Structural acceptance

→ Waterproofing / Air Barrier

→ Insulation

→ Firestop where rated

→ Finish

→ Evidence

→ CLOSED

If any required layer remains incomplete:

PENETRATION = OPEN

That is the important status logic.

11.8 — EMBEDDED ITEMS

Build 2 says these must be identified, coordinated, positioned and secured before concrete permanently conceals them, including sleeves, anchor bolts, inserts, grounding and conduits.

Therefore:

11.8 → G-STR-POUR

Inputs:

Sleeves

- Anchor bolts

- Inserts

- Grounding

- Electrical conduits

- Mechanical embeds

- Other approved cast-ins

↓

Location / elevation / orientation / secure?

↓

Evidence captured?

↓

CONCRETE POUR RELEASE

So 11.8 becomes a direct link from MEP back into Structural.

11.9 — EQUIPMENT BASES

Build 2 defines the base against the actual approved equipment, including size, position, elevation, anchor pattern, service connections, vibration requirements and maintenance clearance.

Therefore:

Equipment Submittal

↓

11.9 Base/Pad

↔ Structure

↔ 8.6 Mechanical Equipment / 9.4 Electrical Equipment

↔ 11.10 Access

↓

Equipment installation

↓

13.7 Start-Up

11.10 — ACCESS & MAINTAINABILITY

This is a global validation node.

Build 2 makes the point that technically functioning work can still be badly constructed if it cannot be maintained. Equipment, valves, dampers, filters, panels, controls and service components need practical access for inspection, operation, removal and maintenance.

Therefore almost any relevant equipment page should have:

Related QC → 11.10 Access & Maintainability

Especially:

8.6 HVAC Equipment
8.8 BAS/Controls
9.4 Electrical Equipment
9.5 Distribution Interfaces
10.4 Dampers
6.9 Access Panels

11.11 — TRADE COORDINATION / CONGESTION

This becomes our conflict hub.

Build 2's objective is to resolve physical conflicts among structural, architectural, mechanical, electrical and fire-protection systems before they cause improvisation, rework or inaccessible construction.

Therefore:

11.11 = globalInterfaceHub

Any activity can link here where:

route conflict
clearance conflict
support conflict
penetration conflict
access conflict
sequence conflict

exists.

12. EXTERNAL WORKS

Build 2 defines:

Survey/layout → excavation → bedding/subgrade → material verification → installation → testing/inspection → pre-concealment evidence → backfill/compaction → final elevation/slope → surface restoration → closure.

| ID | Activity | Before | After | Major Cross-Links | Gate / Testing |
| --- | --- | --- | --- | --- | --- |
| 12.1 | Underground Services | Survey/layout, excavation, bedding | Testing → backfill | 8.1–8.3, 9.x, 12.2, 12.4 | Pre-backfill gate |
| 12.2 | Utility Trenches | Layout / excavation | 12.1 installation → backfill | Earthworks, Underground Services | Bedding/compaction |
| 12.3 | Manholes / Catch Basins / Structures | Excavation/base | Connections/backfill | 12.1, 12.4, 12.7 | Elevation/connections |
| 12.4 | Exterior Drainage | Grading/drainage design | Surface works | 8.3 Storm, 12.3, 12.5–12.8 | Flow/slope/drainage |
| 12.5 | Granular Base/Subbase | Subgrade accepted | Curbs/concrete/asphalt | Earthworks, 12.6–12.8 | Density/compaction |
| 12.6 | Curbs | Base accepted | Asphalt/restoration | 12.5, 12.7, 12.8 | Line/grade |
| 12.7 | Concrete Exterior Works | Base/forms/rebar/embeds | Restoration | 3.x Concrete logic, 12.5/12.6 | Concrete inspection/testing |
| 12.8 | Asphalt | Base/subbase accepted | Final restoration | 12.5/12.6/12.4 | Density/thickness/finish as required |
| 12.9 | Site Restoration | Underground + civil works complete | Final exterior acceptance | All 12.x | Final deficiency inspection |
| 12.10 | Fencing / Gates | Layout/foundations | Security/final acceptance | Concrete, Electrical/Controls where applicable | Operation/security evidence |

External works master dependency

Underground work

↓

G-EXT-01 — PRE-BACKFILL

Location/elevation verified

- Material verified

- Joints/connections inspected

- Required tests passed

- Protection complete

- Identification complete

- Survey/as-built data captured

- Photos captured

↓

RELEASE BACKFILL

↓

Compaction

↓

Granular base

↓

Curbs / concrete / asphalt

↓

Restoration

↓

G-EXT-02 — EXTERNAL WORKS COMPLETION

This prevents the classic problem of discovering something about an underground service after it is buried.

13. TESTING, COMMISSIONING & SYSTEM ACCEPTANCE

This is where the framework changes from:

“Was it installed correctly?”

to:

“Can we prove it performs correctly?”

Build 2 explicitly distinguishes inspection from testing/commissioning and says the inspector's role is to ensure tests are planned, traceable, documented, failures controlled, corrections verified, retests performed and acceptance evidence retained.

The Build 2 workflow is:

Construction complete → readiness confirmed → approved procedure → instruments/personnel ready → test → result → failure controlled → corrective action → retest → specialist acceptance → system closure.

| ID | Activity | Inputs | Output / Links |
| --- | --- | --- | --- |
| 13.1 | Test Readiness | Construction status + prerequisites | Authorization to test |
| 13.2 | Test Documentation | PIE/PRIE, procedure, forms, IDs | Controlled test record |
| 13.3 | Mechanical Testing | 8.10 + mechanical systems | Mechanical acceptance evidence |
| 13.4 | Electrical Testing Interfaces | 9.11 | Specialist electrical acceptance evidence |
| 13.5 | Building Envelope Testing | 4.x + 5.x | Envelope acceptance evidence |
| 13.6 | Functional Testing | Equipment/system installation | Functional result |
| 13.7 | Equipment Start-Up | 8.6 / 9.4 + G-MEP-02 | Operating equipment |
| 13.8 | Integrated/System Testing | Multiple accepted subsystems | Integrated performance result |
| 13.9 | Failed-Test Management | ANY FAILED TEST | Controlled failure/corrective action |
| 13.10 | Retesting | 13.9 correction complete | New test result |
| 13.11 | Acceptance Evidence | All required test/commissioning records | Input to 14.x Closeout |

13.1 — TEST READINESS GATE

G-TST-01

Before testing:

Construction sufficiently complete?

- Approved procedure?

- Correct system/equipment identified?

- Required instruments available/calibrated?

- Required personnel/specialist available?

- Prerequisite inspections accepted?

- Open deficiencies evaluated?

- Test documentation ready?

↓

READY TO TEST

Otherwise:

NOT READY

Build 2 specifically warns that premature testing wastes time and can produce misleading results.

13.9 — FAILED TEST MANAGEMENT

This needs global status logic.

Build 2 says failed tests must never disappear into paperwork: every failure must remain identifiable, controlled, investigated, corrected, retested and traceably closed without losing the original failure record.

Therefore:

ANY TEST

PASS

→ Acceptance evidence

or

FAIL

↓

AUTO-CREATE / LINK 13.9 FAILED TEST

↓

Affected system status:

🔴 FAILED / NOT ACCEPTED

↓

Deficiency/NC as applicable

↓

Corrective Action

↓

Reinspection

↓

13.10 RETEST

↓

PASS?

NO → remains OPEN

YES → acceptance evidence + close failure

Importantly:

Never overwrite the failed result.

History remains:

Test #1 — FAIL

Corrective Action CA-024

Test #2 — PASS

Accepted by X

That is proper traceability.

13.11 — ACCEPTANCE EVIDENCE

This is the testing/commissioning output hub.

Build 2 calls it the final output of the entire testing/commissioning system: evidence that each system was inspected, tested, corrected where necessary, accepted by the appropriate authority and is ready for turnover.

So:

13.3 Mechanical

13.4 Electrical

13.5 Envelope

13.6 Functional

13.7 Start-Up

13.8 Integrated

13.9 Failures

13.10 Retests

↓

13.11 ACCEPTANCE EVIDENCE

↓

14.9 Outstanding Tests

↓

14.14 Final Quality Records

↓

14.15 Turnover

14. DEFICIENCIES, COMPLETION & CLOSEOUT

This is the final closure engine of the entire QMS.

Build 2's completion definition is excellent:

Deficiencies resolved → NCs closed → tests complete → records complete → as-builts current → O&M/warranties/certificates assembled → acceptance evidence traceable → formal turnover achieved.

| ID | Activity | Primary Inputs | Downstream |
| --- | --- | --- | --- |
| 14.1 | Preparatory Deficiency Review | ALL physical work | 14.2 |
| 14.2 | Formal Deficiency Survey | 14.1 + owner/consultant inspection | 14.3 |
| 14.3 | Deficiency Classification | Deficiency record | 14.4 |
| 14.4 | Assignment | Classified deficiency | 14.5 |
| 14.5 | Corrective Work | Assigned issue | 14.6 |
| 14.6 | Reinspection | Corrected work | 14.7 |
| 14.7 | Closure | Accepted correction | Completion status |
| 14.8 | Outstanding NC Closure | NC register / all sections | Final completion |
| 14.9 | Outstanding Test Results | 13.x | Final acceptance |
| 14.10 | Redlines / As-Builts | All installed work + field changes | 14.14 |
| 14.11 | O&M Documentation | Equipment/systems | 14.14 / turnover |
| 14.12 | Certificates / Technical Records | Testing/specialists/authorities | 14.14 |
| 14.13 | Warranties | Equipment/material systems | 14.14 |
| 14.14 | Final Quality Records | Entire QMS | 14.15 |
| 14.15 | Turnover / Acceptance | ALL closure prerequisites | PROJECT QUALITY CLOSED |

DEFICIENCY LOOP

This should be accessible from every inspection page in the application.

Any Activity

↓

DEFICIENCY FOUND

↓

14.3 Classification

↓

14.4 Assignment

↓

14.5 Corrective Work

↓

14.6 Reinspection

↓

Accepted?

NO → corrective loop continues

YES ↓

14.7 Closure

This means we should not build separate deficiency logic inside concrete, masonry, mechanical, electrical, roofing, etc.

Those pages merely create/link a deficiency.

Section 14 owns the common deficiency lifecycle.

That prevents duplication.

NC LOOP

Likewise:

Any Activity

↓

Condition meets NC criteria

↓

NC RECORD

↓

Responsible party / disposition

↓

Corrective action

↓

Verification

↓

Evidence

↓

14.8 NC CLOSURE

An NC can therefore remain linked simultaneously to:

Original activity

- Location

- Trade

- Requirement

- Photos

- Corrective action

- Reinspection

- Final closure

14.10 — AS-BUILT LINKAGE

This should be more dynamic than simply a closeout page.

Any field change that affects final configuration should be capable of carrying:

As-Built Impact = YES

For example:

9.1 conduit route changed

↓

As-Built Impact = YES

↓

Automatically appears under:

14.10 Redlines / As-Builts — OPEN ITEMS

That means the inspector doesn't have to remember four months later:

"Didn't we move that pipe somewhere?"

The system remembers.

14.14 — FINAL QUALITY RECORDS

This is essentially the QMS evidence package, exactly as Build 2 describes it.

Therefore:

14.14 = globalEvidenceHub

It draws from:

Material approvals
Inspections
PIE/PRIE records
Photos
Concrete/testing records
Penetration records
Firestop records
Mechanical tests
Electrical acceptance evidence
Commissioning records
Deficiencies
NCs
Corrective actions
As-builts
O&M
Certificates
Warranties

The user shouldn't manually duplicate those documents into 14.14.

The application should reference/index them from their original records.

That is much cleaner.

14.15 — FINAL TURNOVER GATE

Build 2 explicitly calls 14.15 the final project-quality gate.

So we create:

G-FINAL-01 — TURNOVER / ACCEPTANCE

Physical deficiencies closed?

☐

NCs closed?

☐

Tests complete?

☐

Failed tests resolved/retested?

☐

Commissioning complete?

☐

Acceptance evidence complete?

☐

As-builts complete?

☐

O&M complete?

☐

Certificates/technical records complete?

☐

Warranties complete?

☐

Final quality records indexed?

☐

Outstanding items formally controlled?

☐

↓

ALL REQUIRED = YES

↓

PROJECT / SYSTEM READY FOR TURNOVER

MASTER RELATIONSHIP — 11 → 12 → 13 → 14

And now we can see how the final four sections behave differently from 1–10:

1–10 = WHAT IS BEING BUILT

↓

11 = HOW THE DIFFERENT WORKS INTERACT

↓

12 = EXTERNAL/SITE SYSTEM COMPLETION

↓

13 = DOES THE COMPLETED WORK ACTUALLY PERFORM?

↓

14 = CAN WE PROVE EVERYTHING IS COMPLETE AND HAND IT OVER?

More importantly, however, this isn't strictly linear.

The actual architecture is:

Sections 1–12

↔ 11 Interface Control

↓

13 Testing / Commissioning

↔ 13.9 Failure Loop

↓

14 Deficiency / NC / Completion Control

↺ back to ANY affected Section 1–13

↓

14.14 Evidence Package

↓

14.15 TURNOVER

BUILD 3 — GLOBAL CROSS-LINK TYPES

At this point, I think we can formally freeze the relationship types for the application:

| Relationship | Meaning |
| --- | --- |
| PREREQUISITE | Must occur/be accepted before this activity |
| NEXT | Normal downstream activity |
| INTERFACE | Another system physically/functionally interacts |
| GATE | Status controls permission to proceed |
| PRE-CONCEALMENT | Must be verified before becoming inaccessible |
| TEST | Related test/commissioning activity |
| DEFICIENCY | Links to Section 14 deficiency lifecycle |
| NC | Links to NC control/closure |
| EVIDENCE | Required objective evidence |
| ACCESS | Links to 11.10 maintainability |
| PENETRATION | Links to 11.7 universal penetration workflow |
| AS-BUILT | Final configuration/documentation impact |
| COMMISSIONING | Links to Section 13 |
| TURNOVER | Links toward Section 14 final acceptance |
| INVALIDATES | Later work can revoke a previous accepted status |

That last one—INVALIDATES—is especially important.

For example:

New penetration through accepted rated wall

INVALIDATES → 10.1 Rated Wall acceptance

until:

10.3 Firestop accepted + penetration closed

Likewise:

Equipment relocated

could invalidate:

11.9 Base compatibility
11.10 Access
8/9 service connections
14.10 As-built status

This makes the app behave much more like actual construction.

BUILD 3 IS NOW STRUCTURALLY COMPLETE

We now have the complete relationship architecture from Sections 1 through 14, rather than merely 14 independent technical chapters.

And Build 2 itself confirms that its field-content architecture runs all the way from earthworks through turnover and that the next stage is precisely to transform it into a navigable QMS with cross-references, status logic, gates and field workflows.

So I would stop adding links now. We have enough.

The next step should be to normalize Build 3: consolidate everything we've created for Sections 1–14 into one definitive relationship schema, remove duplicate links, define which links are one-way vs two-way, assign the gate IDs consistently, and establish the exact data fields that Codex will eventually consume. That gives us a clean frozen navigation model before we move into Build 4/5 rather than carrying a huge pile of prose into development.

BUILD 3 – STEP 1 – CANONICAL ACTIVITY REGISTRY

Yes. We should freeze the canonical registry now before touching relationships again.

One adjustment from my earlier proposal: because Build 4 is specifically where we will establish the EN ↔ FR terminology, I do not want to start inventing canonical French names here. That would create exactly the rework we're trying to avoid. Step 1 will therefore freeze the language-neutral ID + canonical English name + section + node tags. Build 4 will later attach the approved French display name to the same immutable ID.

The activity names below preserve the organization established in Build 2. Sections 11–14 are explicitly listed in the source, including the full multidisciplinary, testing/commissioning, and closeout structures.

BUILD 3 — STEP 1

CANONICAL ACTIVITY REGISTRY

Node-tag vocabulary

These are metadata, not necessarily labels the user sees.

| Tag | Meaning |
| --- | --- |
| activity | Standard construction/QC activity |
| umbrella | Coordinates several related activities |
| interface | Exists primarily at the intersection of systems/trades |
| gate | Controls progression to another activity |
| preConcealment | Must be checked before work becomes inaccessible |
| testing | Testing/verification activity |
| commissioning | Commissioning/start-up/system-function activity |
| highControl | Requires unusually rigorous control/traceability |
| traceabilityCritical | Evidence/history is particularly important |
| closeout | Completion/record/turnover activity |
| closeoutHub | Aggregates multiple closeout processes |
| acceptanceGate | Formal readiness/acceptance convergence point |
| specialistInterface | Technical acceptance may require authorized specialist |

A node may have multiple tags.

1 — SITEWORK & EARTHWORKS

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 1.1 | Existing Conditions | activity, traceabilityCritical |
| 1.2 | Survey & Layout | activity, interface |
| 1.3 | Excavation | activity, preConcealment |
| 1.4 | Subgrade | activity, gate, preConcealment |
| 1.5 | Granular Materials | activity, testing, preConcealment |
| 1.6 | Backfill | activity, testing |
| 1.7 | Site Drainage | activity, interface, preConcealment |

2 — SUBSTRUCTURE

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 2.1 | Foundation Formwork | activity, preConcealment |
| 2.2 | Foundation Reinforcement | activity, preConcealment, highControl |
| 2.3 | Embedded Items | activity, interface, preConcealment, traceabilityCritical |
| 2.4 | Pre-Pour Quality Gate | gate, preConcealment, highControl |
| 2.5 | Foundation Concrete | activity, testing, highControl |
| 2.6 | Foundation Concrete Acceptance | gate, testing |
| 2.7 | Foundation Walls | activity, preConcealment |
| 2.8 | Slab-on-Grade | activity, interface, preConcealment, testing |
| 2.9 | Below-Grade Waterproofing | activity, preConcealment, highControl |
| 2.10 | Foundation Insulation | activity, preConcealment |
| 2.11 | Foundation Drainage | activity, interface, preConcealment, testing |
| 2.12 | Backfill Against Structure | activity, gate |

The integrated sequence in Build 2 treats formwork, reinforcement, embeds, pre-pour, concrete, waterproofing, insulation, drainage and backfill as dependent controls rather than isolated checklists.

3 — SUPERSTRUCTURE

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 3.1 | Cast-in-Place Concrete | activity, interface, testing, preConcealment |
| 3.2 | Structural Steel — Materials | activity, traceabilityCritical |
| 3.3 | Structural Steel — Erection | activity, interface |
| 3.4 | Bolted Connections | activity, testing, preConcealment |
| 3.5 | Welding | activity, testing, specialistInterface, preConcealment |
| 3.6 | Steel Protection | activity, testing, preConcealment |
| 3.7 | Structural Masonry | activity, interface, testing, preConcealment |
| 3.8 | Precast Elements — If Applicable | activity, interface, testing |

4 — BUILDING ENVELOPE

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 4.1 | Exterior Wall Assemblies | umbrella, interface, highControl |
| 4.2 | Air Barrier | activity, interface, preConcealment, highControl |
| 4.3 | Vapour Barrier | activity, interface, preConcealment |
| 4.4 | Thermal Insulation | activity, interface, preConcealment |
| 4.5 | Exterior Sheathing | activity, preConcealment |
| 4.6 | Exterior Masonry / Veneer | activity, interface, preConcealment |
| 4.7 | Exterior Cladding / Panels | activity, interface, preConcealment |
| 4.8 | Windows / Glazing | activity, interface, testing, highControl |
| 4.9 | Exterior Doors | activity, interface, testing |
| 4.10 | Sealants | activity, interface, testing |

Build 2 expressly treats the envelope as an interconnected assembly with critical interfaces at foundations, roofs, openings, structure and MEP penetrations rather than as separate material layers.

5 — ROOFING

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 5.1 | Roof Deck / Substrate | activity, gate, preConcealment |
| 5.2 | Vapour / Air Control Layer | activity, interface, gate, preConcealment, highControl |
| 5.3 | Roof Insulation | activity, gate, preConcealment |
| 5.4 | Roofing Membrane | activity, interface, gate, highControl |
| 5.5 | Flashings & Terminations | activity, interface, highControl |
| 5.6 | Roof Penetrations | interface, preConcealment, highControl, traceabilityCritical |
| 5.7 | Curbs & Equipment Interfaces | interface, preConcealment |
| 5.8 | Roof Drains | interface, testing, preConcealment |
| 5.9 | Roofing Testing / Final Inspection | testing, gate, acceptanceGate |

Build 2 already establishes distinct roofing gates from deck acceptance through control layers, insulation, membrane/interfaces and final testing.

6 — INTERIOR ARCHITECTURAL CONSTRUCTION

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 6.1 | Interior Masonry | activity, interface, preConcealment |
| 6.2 | Metal Stud Framing | activity, interface, preConcealment |
| 6.3 | Interior Insulation | activity, preConcealment |
| 6.4 | Gypsum Board | activity, gate |
| 6.5 | Fire-Rated Assemblies | umbrella, interface, preConcealment, highControl |
| 6.6 | Interior Doors & Frames | activity, interface |
| 6.7 | Door Hardware | activity, interface, testing |
| 6.8 | Ceilings | activity, interface, gate, preConcealment |
| 6.9 | Access Panels | interface, preConcealment |

7 — FINISHES

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 7.1 | Concrete Floor Preparation | activity, testing |
| 7.2 | Floor Finishes | activity, testing |
| 7.3 | Wall Finishes | activity |
| 7.4 | Painting / Coatings | activity, testing |
| 7.5 | Architectural Sealants | activity, interface, testing |
| 7.6 | Specialty Finishes | activity |
| 7.7 | Final Architectural Deficiency Inspection | closeout, closeoutHub |

8 — MECHANICAL SERVICES

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 8.1 | Plumbing — Domestic Water | activity, testing, preConcealment |
| 8.2 | Sanitary Drainage | activity, testing, preConcealment |
| 8.3 | Storm Drainage | activity, interface, testing, preConcealment |
| 8.4 | Process / Equipment Piping — Where Applicable | activity, interface, testing |
| 8.5 | HVAC Ductwork | activity, interface, testing, preConcealment |
| 8.6 | HVAC Equipment | activity, interface, commissioning |
| 8.7 | Mechanical Insulation | activity, preConcealment |
| 8.8 | Mechanical Controls / BAS Interfaces | interface, commissioning, specialistInterface |
| 8.9 | Mechanical Penetrations | interface, gate, preConcealment, highControl, traceabilityCritical |
| 8.10 | Mechanical Testing | testing, gate, specialistInterface |
| 8.11 | Mechanical Identification | activity, closeout |

The mechanical workflow in the source explicitly moves from approved system and installation through supports, penetrations, testing, insulation, identification and commissioning.

9 — ELECTRICAL BUILDING SERVICES

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 9.1 | Conduits / Raceways | activity, interface, preConcealment |
| 9.2 | Cable Trays | activity, interface |
| 9.3 | Supports / Hangers | activity, interface |
| 9.4 | Electrical Equipment Installation | activity, interface, specialistInterface |
| 9.5 | Building Distribution Interfaces | interface, specialistInterface |
| 9.6 | Grounding / Bonding — Within Assigned Inspection Scope | interface, testing, preConcealment, specialistInterface |
| 9.7 | Lighting | activity, interface, testing |
| 9.8 | Emergency Lighting | activity, interface, testing, specialistInterface |
| 9.9 | Electrical Penetrations | interface, gate, preConcealment, highControl, traceabilityCritical |
| 9.10 | Identification / Labels | activity, closeout |
| 9.11 | Electrical Testing Interfaces | testing, gate, specialistInterface, traceabilityCritical |

10 — FIRE & LIFE-SAFETY CONSTRUCTION

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 10.1 | Fire-Rated Walls | activity, interface, gate, preConcealment, highControl |
| 10.2 | Fire-Rated Floors / Ceilings | activity, interface, gate, preConcealment, highControl |
| 10.3 | Firestopping | interface, gate, preConcealment, highControl, traceabilityCritical |
| 10.4 | Fire / Smoke Dampers | interface, testing, preConcealment, specialistInterface |
| 10.5 | Fire-Rated Doors | interface, testing, highControl |
| 10.6 | Fire-Alarm Physical Installation Interfaces | interface, testing, specialistInterface |
| 10.7 | Emergency / Life-Safety Interfaces | umbrella, interface, testing, acceptanceGate, specialistInterface |
| 10.8 | Fire Protection Systems — If Applicable | activity, interface, testing, specialistInterface |

11 — MULTIDISCIPLINARY INTERFACES

This section is intentionally different: almost every node is an interface node. Build 2 describes it as the place where adjacent and overlapping systems are coordinated so that one trade does not compromise another.

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 11.1 | Structural ↔ Architectural | interface |
| 11.2 | Structural ↔ Mechanical | interface |
| 11.3 | Structural ↔ Electrical | interface |
| 11.4 | Envelope ↔ Mechanical | interface, highControl |
| 11.5 | Envelope ↔ Electrical | interface, highControl |
| 11.6 | Architectural ↔ MEP | interface, preConcealment |
| 11.7 | Universal Penetrations | umbrella, interface, gate, preConcealment, highControl, traceabilityCritical |
| 11.8 | Embedded Items | interface, gate, preConcealment, traceabilityCritical |
| 11.9 | Equipment Bases / Housekeeping Pads | interface, gate |
| 11.10 | Access & Maintainability | interface, acceptanceGate |
| 11.11 | Trade Coordination / Congestion | umbrella, interface |

Build 2 particularly elevates Universal Penetrations, Access & Maintainability, and Trade Coordination/Congestion.

12 — EXTERNAL WORKS

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 12.1 | Underground Services | activity, interface, testing, preConcealment, traceabilityCritical |
| 12.2 | Utility Trenches | activity, preConcealment |
| 12.3 | Manholes / Catch Basins / Structures | activity, interface, testing |
| 12.4 | Exterior Drainage | activity, interface, testing |
| 12.5 | Granular Base / Subbase | activity, testing, gate |
| 12.6 | Curbs | activity |
| 12.7 | Concrete Exterior Works | activity, testing |
| 12.8 | Asphalt | activity, testing |
| 12.9 | Site Restoration | closeout, closeoutHub |
| 12.10 | Fencing / Gates — If Applicable | activity, interface, testing |

The source gives the external-works sequence as survey/layout through excavation, installation and testing, pre-concealment evidence, backfill/compaction, final elevation and restoration.

13 — TESTING, COMMISSIONING & SYSTEM ACCEPTANCE

This section is mostly process nodes rather than construction nodes. Build 2 defines it as demonstrating through controlled and traceable testing that completed systems perform as required before turnover.

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 13.1 | Test Readiness | testing, gate, acceptanceGate |
| 13.2 | Test Documentation | testing, traceabilityCritical |
| 13.3 | Mechanical Testing | testing, specialistInterface |
| 13.4 | Electrical Testing Interfaces | testing, specialistInterface |
| 13.5 | Building Envelope Testing | testing, specialistInterface |
| 13.6 | Functional Testing | testing, commissioning, specialistInterface |
| 13.7 | Equipment Start-Up | testing, commissioning, specialistInterface |
| 13.8 | Integrated / System Testing — Where Applicable | testing, commissioning, interface, specialistInterface, highControl |
| 13.9 | Failed-Test Management | testing, gate, traceabilityCritical, highControl |
| 13.10 | Retesting | testing, gate, traceabilityCritical |
| 13.11 | Acceptance Evidence | testing, closeoutHub, acceptanceGate, traceabilityCritical |

Build 2 itself marks Failed-Test Management and Acceptance Evidence as especially important because they move quality control from merely witnessing tests toward controlling overall system status.

14 — DEFICIENCIES, COMPLETION & CLOSEOUT

| ID | Canonical English Name | Node Tags |
| --- | --- | --- |
| 14.1 | Preparatory Deficiency Review | closeout, closeoutHub |
| 14.2 | Formal Deficiency Survey | closeout, traceabilityCritical |
| 14.3 | Deficiency Classification | closeout, gate |
| 14.4 | Assignment | closeout |
| 14.5 | Corrective Work | closeout, activity |
| 14.6 | Reinspection | closeout, testing, gate |
| 14.7 | Closure | closeout, acceptanceGate |
| 14.8 | Outstanding NC Closure | closeout, highControl, traceabilityCritical, acceptanceGate |
| 14.9 | Outstanding Test Results | closeout, testing, acceptanceGate |
| 14.10 | Redlines / As-Builts | closeout, traceabilityCritical |
| 14.11 | O&M Documentation | closeout |
| 14.12 | Certificates / Technical Records | closeout, traceabilityCritical |
| 14.13 | Warranties | closeout |
| 14.14 | Final Quality Records | closeout, closeoutHub, traceabilityCritical |
| 14.15 | Turnover / Acceptance | closeout, acceptanceGate, highControl |

Build 2 defines project completion as deficiency resolution, NC closure, completed testing and records, current as-builts, assembled O&M/warranty/certificate documentation, traceable acceptance evidence and formal turnover. It expressly identifies 14.15 as the final project-quality gate.

CANONICAL VIRTUAL GATE REGISTRY

There is one important distinction.

Some gates are not Build 2 numbered activities. They are navigation/process objects we identified while connecting the numbered activities. They need their own namespace so we never confuse them with content sections.

I recommend prefix:

G-

rather than giving them fake 1–14 numbers.

| Gate ID | Canonical Name | Type |
| --- | --- | --- |
| G-STR-01 | Structural Pre-Pour Gate | gate, preConcealment |
| G-INT-01 | Interior Wall / Ceiling Pre-Concealment Gate | gate, preConcealment |
| G-MEP-01 | MEP Pre-Concealment Gate | gate, preConcealment |
| G-MEP-02 | Equipment Commissioning Readiness Gate | gate, commissioning |
| G-ENV-01 | Envelope Pre-Concealment Gate | gate, preConcealment |
| G-ROOF-01 | Roof Assembly Progression Gate | gate, preConcealment |
| G-EXT-01 | Underground / Pre-Backfill Gate | gate, preConcealment |
| G-EXT-02 | External Works Completion Gate | gate, acceptanceGate |
| G-TST-01 | Test Readiness Gate | gate, testing |
| G-LS-01 | Life-Safety Integrated Readiness Gate | gate, testing, acceptanceGate |
| G-FINAL-01 | Final Turnover / Acceptance Gate | gate, closeout, acceptanceGate |

Note the distinction between 2.4 Pre-Pour Quality Gate and G-STR-01:

- 2.4 is actual Build 2 content.

- G-STR-01 is the software/navigation logic that can aggregate 2.1 + 2.2 + 2.3 + relevant 8/9/11 items before permitting the concrete workflow to proceed.

We should never conflate content nodes with application logic nodes.

That distinction will save us a lot of trouble later.

IDENTIFIER RULES — FREEZE THESE NOW

I recommend we make these immutable:

Content node

section.subsection

Examples:

4.2
8.9
13.11

Gate

G-DOMAIN-##

Example:

G-MEP-01

Later instance records

When we eventually need actual field examples/records, use another namespace entirely.

For example:

PEN-0001 — penetration instance
FS-0001 — firestop instance
DEF-0001 — deficiency
NC-0001 — non-conformance
TST-0001 — test
EQUIP-0001 — equipment instance

But those are not part of the universal guide MVP right now. I mention them only so we don't later accidentally use activity IDs for field records.

WHAT WE HAVE NOW FROZEN

The architecture now recognizes three fundamentally different things:

1. CONTENT NODES

The 139 numbered Build 2 activities.

These contain the knowledge.

2. LOGIC NODES

The G-* gates.

These control navigation/readiness relationships.

3. RELATIONSHIPS

These connect content and gates.

Those come in Step 2.

That gives us the clean architecture:

Content ≠ Logic ≠ Relationship

And that is exactly what we want before Codex sees any implementation specification.

One deliberate omission: French

The registry should eventually contain fields such as:

title.en
title.fr

But for now:

title.en = frozen

title.fr = null

We populate title.fr during Build 4 after we establish the Québec construction terminology rules.

This avoids translating 139 names today and then discovering during Build 4 that we want a different terminology convention.

STEP 1 STATUS

Sections 1–14 canonical IDs: FROZEN ✓

Canonical English names: FROZEN ✓

Node-tag taxonomy: FROZEN ✓

Virtual-gate namespace: FROZEN ✓

Content vs logic distinction: FROZEN ✓

French names: intentionally deferred to Build 4 ✓

Relationship edges: NOT YET normalized

So Step 1 is complete.

Step 2 is where this gets really interesting: we take the hundreds of links we've established and reduce them into a single canonical Relationship Registry with source node, relationship type, target node, directionality, conditions, and reciprocal behavior. That becomes the actual graph Codex will eventually implement.

Yes. Step 2 is where we turn the links we created into one normalized graph that Codex can implement without duplication or contradictions.

The most important normalization decision is this:

We should not store both “Before” and “After” links separately.

If 2.5 Foundation Concrete REQUIRES 2.4 Pre-Pour Quality Gate, the app can automatically derive:

- Foundation Concrete → Before: Pre-Pour Quality Gate

- Pre-Pour Quality Gate → After: Foundation Concrete

Likewise, an INTERFACES_WITH relationship is reciprocal automatically.

That will eliminate hundreds of redundant links and make maintenance far safer.

Build 2 itself supports this dependency-based logic: substructure is explicitly structured as a sequence of prerequisites, and the framework repeatedly uses pre-concealment and testing gates before downstream work proceeds.

BUILD 3 — STEP 2

CANONICAL RELATIONSHIP REGISTRY

A. Canonical stored relationship types

I would reduce the underlying graph to nine stored relationship types.

| Relationship | Direction | Meaning |
| --- | --- | --- |
| REQUIRES | A → B | A normally depends on B being sufficiently complete/accepted |
| INTERFACES_WITH | A ↔ B | Physical/functional multidisciplinary interaction |
| GATED_BY | A → Gate | A cannot logically progress until gate conditions are satisfied |
| TESTED_BY | A → Test | A has related testing/acceptance activity |
| COMMISSIONED_BY | A → Commissioning | A participates in start-up/functional/integrated commissioning |
| PENETRATION_MANAGED_BY | A → 11.7 | Penetration condition falls under universal penetration control |
| ACCESS_CHECKED_BY | A → 11.10 | Maintainability/access review applies |
| CLOSES_THROUGH | A → Closeout node | Completion feeds a specific closeout process |
| AS_BUILT_FEEDS | A → 14.10 | Field configuration may require redline/as-built update |

Everything else can be derived or inherited.

B. Relationships we do NOT store repeatedly

These remain part of the app behavior but shouldn't produce thousands of edges.

BEFORE

Derived from:

A REQUIRES B

B appears under A's Before.

AFTER

Reverse lookup of REQUIRES.

A appears under B's After.

RELATED QC

Generated from all:

- INTERFACES_WITH

- TESTED_BY

- PENETRATION_MANAGED_BY

- ACCESS_CHECKED_BY

- gate associations.

PRE-CONCEALMENT

This should be a node tag + gate rule, not a separate relationship repeated everywhere.

DEFICIENCY

Universal inherited behavior:

Any inspectable node → may create deficiency → Section 14 lifecycle.

NC

Universal inherited behavior:

Any node → may create NC where project criteria require → 14.8 closure.

EVIDENCE

Every node contains its own evidence requirements. No graph edge required.

TURNOVER

Derived through Section 14.

INVALIDATES

Important enough that we'll create a separate invalidation-rule registry, rather than pretending it is an ordinary construction relationship.

C. Relationship object

Each stored relationship should eventually look conceptually like:

source

relationship

target

condition

strength

reciprocal

notes

For example:

source: 2.5

relationship: REQUIRES

target: 2.4

condition: before foundation concrete placement

strength: hard

reciprocal: derived

The app doesn't need to display any of that technical metadata.

D. Dependency strength

We need one additional field:

| Strength | Meaning |
| --- | --- |
| hard | Normally cannot proceed without satisfying dependency |
| conditional | Applies only where particular assembly/system exists |
| coordination | Does not necessarily block work but must be considered |

This prevents:

“Everything is a hold point.”

For example:

2.5 Foundation Concrete REQUIRES 2.4 Pre-Pour Gate

= hard

Whereas:

4.8 Windows INTERFACES_WITH 4.6 Exterior Masonry

= conditional/coordination

because the particular envelope may not use masonry.

E. SECTION 1 — SITEWORK & EARTHWORKS

Dependencies

| Source | Relation | Target | Strength |
| --- | --- | --- | --- |
| 1.2 Survey & Layout | REQUIRES | 1.1 Existing Conditions | hard |
| 1.3 Excavation | REQUIRES | 1.2 Survey & Layout | hard |
| 1.4 Subgrade | REQUIRES | 1.3 Excavation | hard |
| 1.5 Granular Materials | REQUIRES | 1.4 Subgrade | hard |
| 1.6 Backfill | REQUIRES | buried work acceptance | conditional |
| 1.7 Site Drainage | REQUIRES | 1.3 Excavation | conditional |
| 1.7 Site Drainage | REQUIRES | 1.2 Survey & Layout | hard |

Interfaces

| Node A | Relation | Node B |
| --- | --- | --- |
| 1.3 Excavation | INTERFACES_WITH | 12.2 Utility Trenches |
| 1.3 Excavation | INTERFACES_WITH | 12.1 Underground Services |
| 1.4 Subgrade | INTERFACES_WITH | 2.8 Slab-on-Grade |
| 1.5 Granular Materials | INTERFACES_WITH | 2.8 Slab-on-Grade |
| 1.6 Backfill | INTERFACES_WITH | 2.12 Backfill Against Structure |
| 1.7 Site Drainage | INTERFACES_WITH | 2.11 Foundation Drainage |
| 1.7 Site Drainage | INTERFACES_WITH | 12.4 Exterior Drainage |

Testing

1.4 → geotechnical acceptance where required

1.5 TESTED_BY → compaction/density testing

1.6 TESTED_BY → compaction/density testing

Those generic tests need not become numbered Build 13 nodes unless they participate in formal commissioning.

F. SECTION 2 — SUBSTRUCTURE

Core dependency chain

| Source | Relation | Target | Strength |
| --- | --- | --- | --- |
| 2.1 Foundation Formwork | REQUIRES | 1.4 Subgrade | conditional |
| 2.2 Foundation Reinforcement | REQUIRES | 2.1 Foundation Formwork | hard |
| 2.3 Embedded Items | REQUIRES | coordinated form/rebar condition | hard |
| 2.4 Pre-Pour Quality Gate | REQUIRES | 2.1 Foundation Formwork | hard |
| 2.4 | REQUIRES | 2.2 Foundation Reinforcement | hard |
| 2.4 | REQUIRES | 2.3 Embedded Items | hard |
| 2.5 Foundation Concrete | REQUIRES | 2.4 Pre-Pour Quality Gate | hard |
| 2.6 Foundation Concrete Acceptance | REQUIRES | 2.5 Foundation Concrete | hard |
| 2.7 Foundation Walls | REQUIRES | relevant accepted foundation work | hard |
| 2.8 Slab-on-Grade | REQUIRES | 1.4 Subgrade | hard |
| 2.8 | REQUIRES | 1.5 Granular Materials | hard |
| 2.9 Below-Grade Waterproofing | REQUIRES | accepted foundation substrate | hard |
| 2.10 Foundation Insulation | REQUIRES | 2.9 Waterproofing where assembly requires | conditional |
| 2.11 Foundation Drainage | REQUIRES | foundation geometry/subgrade ready | hard |
| 2.12 Backfill Against Structure | REQUIRES | 2.9 Waterproofing | conditional |
| 2.12 | REQUIRES | 2.10 Foundation Insulation | conditional |
| 2.12 | REQUIRES | 2.11 Foundation Drainage | conditional |

Gate connections

2.5 GATED_BY → G-STR-01

2.12 GATED_BY → G-EXT-01 where buried/interface conditions apply.

Interfaces

2.3 Embedded Items INTERFACES_WITH 11.8 Embedded Items

2.3 ↔ 9.1 Conduits/Raceways

2.3 ↔ 9.6 Grounding/Bonding

2.3 ↔ Mechanical sleeves/services

2.8 ↔ 9.1 Embedded Conduits

2.8 ↔ Mechanical drains/sleeves

2.9 ↔ 4.2 Air Barrier

2.11 ↔ 1.7 Site Drainage

Testing

2.5 TESTED_BY → concrete testing

2.8 TESTED_BY → concrete testing

G. SECTION 3 — SUPERSTRUCTURE

Dependencies

3.1 Cast-in-Place Concrete REQUIRES structural pre-pour prerequisites

3.3 Structural Steel Erection REQUIRES 3.2 Steel Materials

3.3 Structural Steel Erection REQUIRES accepted supporting structure

3.4 Bolted Connections REQUIRES 3.3 Erection

3.5 Welding REQUIRES 3.3 Erection

3.6 Steel Protection REQUIRES 3.4 and/or 3.5 connection completion

3.7 Structural Masonry REQUIRES accepted support

3.8 Precast Elements REQUIRES accepted support/anchors

Interfaces

3.1 ↔ 11.8 Embedded Items

3.1 ↔ 9.1 Conduits

3.1 ↔ 9.6 Grounding

3.3 ↔ 4.1 Exterior Wall Assemblies

3.3 ↔ 11.9 Equipment Bases/supports where applicable

3.7 ↔ 8.9 Mechanical Penetrations

3.7 ↔ 9.9 Electrical Penetrations

3.7 ↔ 10.3 Firestopping

Testing

3.1 TESTED_BY → concrete testing

3.4 TESTED_BY → connection inspection/testing

3.5 TESTED_BY → welding inspection/NDT

3.7 TESTED_BY → masonry/grout testing

H. SECTION 4 — BUILDING ENVELOPE

Dependencies

4.1 Exterior Wall Assemblies REQUIRES supporting structure

4.2 Air Barrier REQUIRES accepted substrate/sheathing

4.4 Thermal Insulation REQUIRES underlying control layer as assembly dictates

4.6 Exterior Masonry REQUIRES envelope layers/supports sufficiently complete

4.7 Cladding REQUIRES underlying control layers/substructure

4.8 Windows REQUIRES approved/prepared opening

4.9 Exterior Doors REQUIRES approved/prepared opening

4.10 Sealants REQUIRES prepared adjacent substrates

Interfaces

4.2 ↔ 2.9 Below-Grade Waterproofing

4.2 ↔ 5.2 Roof Vapour/Air Layer

4.2 ↔ 4.8 Windows

4.2 ↔ 4.9 Exterior Doors

4.2 ↔ 8.9 Mechanical Penetrations

4.2 ↔ 9.9 Electrical Penetrations

4.3 ↔ 5.2

4.3 ↔ 8.9

4.3 ↔ 9.9

4.4 ↔ 4.8

4.4 ↔ 4.9

4.4 ↔ 5.3 Roof Insulation

4.6 ↔ 4.8

4.6 ↔ 4.9

4.6 ↔ 4.10

4.7 ↔ 4.8

4.7 ↔ 4.9

4.7 ↔ 4.10

Testing

4.8 Windows TESTED_BY → 13.5 Building Envelope Testing

4.9 Exterior Doors TESTED_BY → 13.5 where specified

4.1 Exterior Wall Assemblies TESTED_BY → 13.5 where applicable

Gate

Envelope activities with concealed control layers:

GATED_BY → G-ENV-01

The source specifically emphasizes continuity at interfaces and openings, particularly for the air barrier.

I. SECTION 5 — ROOFING

The roofing dependency chain is strong enough to store directly:

5.2 REQUIRES 5.1

5.3 REQUIRES 5.2

5.4 REQUIRES 5.3

5.5 REQUIRES 5.4

5.6 REQUIRES roof assembly/opening readiness

5.7 REQUIRES structural support + coordinated equipment

5.8 REQUIRES roof/piping coordination

5.9 REQUIRES 5.1–5.8 as applicable

Gate

5.2 GATED_BY G-ROOF-01

5.3 GATED_BY G-ROOF-01

5.4 GATED_BY G-ROOF-01

5.9 GATED_BY G-ROOF-01

Build 2 itself establishes these roof progression gates explicitly.

Interfaces

5.2 ↔ 4.2

5.3 ↔ 4.4

5.5 ↔ 4.x Envelope

5.6 ↔ 8.9

5.6 ↔ 9.9

5.6 PENETRATION_MANAGED_BY → 11.7

5.7 ↔ 8.6 HVAC Equipment

5.7 ↔ 9.4 Electrical Equipment where rooftop

5.7 ACCESS_CHECKED_BY → 11.10

5.8 ↔ 8.3 Storm Drainage

Testing

5.9 TESTED_BY → 13.5 Building Envelope Testing

J. SECTION 6 — INTERIOR ARCHITECTURAL

Dependencies

6.3 Interior Insulation REQUIRES 6.2 Metal Stud Framing

6.4 Gypsum Board REQUIRES 6.2 Framing

6.4 REQUIRES relevant 6.3 Insulation

6.6 Interior Doors/Frames REQUIRES wall/opening readiness

6.7 Door Hardware REQUIRES 6.6

6.8 Ceilings REQUIRES above-ceiling readiness

6.9 Access Panels REQUIRES maintainable item/location identified

Gates

6.4 GATED_BY → G-INT-01

6.8 GATED_BY → G-INT-01

Build 2 explicitly makes wall/ceiling closure dependent on concealed MEP, fire integrity, access and other prerequisites.

Interfaces

6.1 ↔ 10.1 Fire-Rated Walls

6.1 ↔ 8.9

6.1 ↔ 9.9

6.2 ↔ MEP rough-ins

6.5 ↔ 10.1

6.5 ↔ 10.2

6.5 ↔ 10.3

6.6 ↔ 10.5 Fire-Rated Doors

6.7 ↔ 10.5

6.7 ↔ electrical/access-control interfaces

6.8 ↔ 8.5 HVAC Ductwork

6.8 ↔ 9.7 Lighting

6.8 ↔ 10.6 Fire Alarm

6.8 ↔ 10.8 Fire Protection

6.8 ↔ 6.9 Access Panels

6.9 ACCESS_CHECKED_BY → 11.10

K. SECTION 7 — FINISHES

Dependencies

7.1 Concrete Floor Preparation REQUIRES 2.8 Slab-on-Grade or accepted slab

7.2 Floor Finishes REQUIRES 7.1

7.3 Wall Finishes REQUIRES accepted wall substrate

7.4 Painting/Coatings REQUIRES accepted substrate

7.5 Architectural Sealants REQUIRES finished/prepared adjacent substrates

7.6 Specialty Finishes REQUIRES approved substrate/system

7.7 Final Architectural Deficiency Inspection REQUIRES 7.1–7.6 substantially complete

Closeout

7.7 CLOSES_THROUGH → 14.1 Preparatory Deficiency Review

and/or

7.7 CLOSES_THROUGH → 14.2 Formal Deficiency Survey

depending on how we later present the workflow.

L. SECTION 8 — MECHANICAL

Core dependencies

8.7 Mechanical Insulation REQUIRES required 8.10 Mechanical Testing where testing precedes insulation

8.8 Controls/BAS REQUIRES related equipment/devices sufficiently installed

8.10 Mechanical Testing REQUIRES relevant mechanical installation complete enough to test

8.11 Identification REQUIRES final system/equipment configuration

Interfaces

8.3 ↔ 5.8 Roof Drains

8.3 ↔ 12.4 Exterior Drainage

8.4 ↔ 8.6 Equipment

8.5 ↔ 8.6 Equipment

8.5 ↔ 6.8 Ceilings

8.5 ↔ 10.4 Fire/Smoke Dampers

8.6 ↔ 5.7 Roof Curbs

8.6 ↔ 9.5 Building Distribution Interfaces

8.6 ↔ 8.8 Controls

8.6 ACCESS_CHECKED_BY → 11.10

8.8 ↔ 9.5

8.8 ↔ 10.4

Penetration

8.9 PENETRATION_MANAGED_BY → 11.7

8.9 ↔ 4.x Envelope where external

8.9 ↔ 5.6 Roof Penetrations

8.9 ↔ 6.x Interior assemblies

8.9 ↔ 10.3 Firestopping

Testing

8.1 TESTED_BY → 8.10

8.2 TESTED_BY → 8.10

8.3 TESTED_BY → 8.10

8.4 TESTED_BY → 8.10

8.5 TESTED_BY → 8.10

8.6 COMMISSIONED_BY → 13.7 Equipment Start-Up

8.6 COMMISSIONED_BY → 13.6 Functional Testing

8.8 COMMISSIONED_BY → 13.6

8.10 TESTED_BY → 13.3 Mechanical Testing

M. SECTION 9 — ELECTRICAL

Dependencies

9.2 Cable Trays REQUIRES support/route readiness

9.4 Electrical Equipment Installation REQUIRES equipment area/base readiness

9.5 Distribution Interfaces REQUIRES related equipment installation

9.10 Identification REQUIRES final equipment/system naming

9.11 Electrical Testing Interfaces REQUIRES construction sufficiently complete

Structural interfaces

9.1 ↔ 11.3 Structural ↔ Electrical

9.1 ↔ 11.8 Embedded Items

9.3 ↔ Structure

9.4 ↔ 11.9 Equipment Bases

9.6 ↔ concrete/structural steel

Mechanical interfaces

9.5 ↔ 8.6 HVAC Equipment

9.5 ↔ 8.8 BAS

Architectural interfaces

9.7 ↔ 6.8 Ceilings

9.8 ↔ 10.7 Emergency/Life-Safety

Penetrations

9.9 PENETRATION_MANAGED_BY → 11.7

9.9 ↔ 4.x Envelope

9.9 ↔ 5.6 Roof Penetrations

9.9 ↔ 6.x Interior assemblies

9.9 ↔ 10.3 Firestopping

Testing/commissioning

9.4 TESTED_BY → 9.11

9.6 TESTED_BY → 9.11

9.8 TESTED_BY → 9.11

9.11 TESTED_BY → 13.4 Electrical Testing Interfaces

9.4 COMMISSIONED_BY → 13.7/13.6 where applicable

N. SECTION 10 — FIRE & LIFE SAFETY

This area uses especially strong interface relationships.

Rated construction

10.1 ↔ 6.5 Fire-Rated Assemblies

10.1 ↔ 8.9 Mechanical Penetrations

10.1 ↔ 9.9 Electrical Penetrations

10.1 ↔ 10.3 Firestopping

10.1 ↔ 10.5 Fire-Rated Doors

10.2 ↔ 6.8 Ceilings

10.2 ↔ 10.3 Firestopping

10.2 ↔ 10.4 Fire/Smoke Dampers

Firestop

10.3 PENETRATION_MANAGED_BY → 11.7

10.3 GATED_BY → G-INT-01 where wall/ceiling closure involved.

Build 2 explicitly treats firestop as a complete approved system and one of the highest-control pre-concealment activities.

Dampers

10.4 ↔ 8.5 Ductwork

10.4 ↔ 8.8 BAS

10.4 ↔ 10.6 Fire Alarm

10.4 ACCESS_CHECKED_BY → 11.10

10.4 COMMISSIONED_BY → 13.6

10.4 COMMISSIONED_BY → 13.8 where integrated.

Fire doors

10.5 ↔ 6.6 Doors/Frames

10.5 ↔ 6.7 Hardware

10.5 COMMISSIONED_BY → 13.6

10.5 → 10.7 Life-Safety Interfaces

Fire alarm

10.6 ↔ 9.x Electrical

10.6 ↔ 10.4 Dampers

10.6 COMMISSIONED_BY → 13.8

Life safety

10.7 GATED_BY → G-LS-01

10.7 COMMISSIONED_BY → 13.8

Fire protection

10.8 ↔ 10.3 Firestopping

10.8 ↔ 6.8 Ceilings

10.8 ↔ 10.6 Fire Alarm

10.8 COMMISSIONED_BY → 13.6/13.8

Build 2 explicitly says 10.7 links several systems rather than representing one trade.

O. SECTION 11 — MULTIDISCIPLINARY

This section generally doesn't need many REQUIRES edges because it is primarily a relationship hub.

Interface pairs

11.1 Structural ↔ Architectural

targets:

3.x ↔ 4.x/5.x/6.x/7.x

11.2 Structural ↔ Mechanical

targets:

3.x ↔ 8.x

11.3 Structural ↔ Electrical

targets:

3.x ↔ 9.x

11.4 Envelope ↔ Mechanical

targets:

4.x/5.x ↔ 8.x

11.5 Envelope ↔ Electrical

targets:

4.x/5.x ↔ 9.x

11.6 Architectural ↔ MEP

targets:

6.x/7.x ↔ 8.x/9.x/10.x

These hubs can be reached contextually rather than requiring every single possible pair to be stored individually.

Universal Penetrations

8.9 PENETRATION_MANAGED_BY → 11.7

9.9 → 11.7

5.6 → 11.7

10.3 → 11.7

Embedded items

2.3 ↔ 11.8

9.1 ↔ 11.8

9.6 ↔ 11.8

Equipment bases

8.6 ↔ 11.9

9.4 ↔ 11.9

Maintainability

8.6 ACCESS_CHECKED_BY 11.10

8.8 ACCESS_CHECKED_BY 11.10

9.4 ACCESS_CHECKED_BY 11.10

9.5 ACCESS_CHECKED_BY 11.10

10.4 ACCESS_CHECKED_BY 11.10

6.9 ACCESS_CHECKED_BY 11.10

Congestion

Relevant coordination-heavy nodes:

8.5 ↔ 11.11

9.2 ↔ 11.11

9.1 ↔ 11.11

10.8 ↔ 11.11

6.8 ↔ 11.11

But the app should also allow any node to reach 11.11 from Interfaces → Trade Coordination.

P. SECTION 12 — EXTERNAL WORKS

Dependencies

12.1 Underground Services REQUIRES 12.2 Utility Trenches

12.3 Manholes/Catch Basins REQUIRES excavation/base readiness

12.4 Exterior Drainage REQUIRES related underground drainage infrastructure

12.5 Granular Base/Subbase REQUIRES accepted subgrade

12.6 Curbs REQUIRES 12.5

12.7 Exterior Concrete REQUIRES 12.5

12.8 Asphalt REQUIRES 12.5

12.9 Site Restoration REQUIRES major external works substantially complete

12.10 Fencing/Gates REQUIRES layout/foundation readiness

Interfaces

12.1 ↔ 8.1–8.3

12.1 ↔ electrical underground services

12.3 ↔ 12.4

12.4 ↔ 8.3 Storm Drainage

12.4 ↔ 1.7 Site Drainage

Gates

12.1 GATED_BY → G-EXT-01 before backfill.

12.9 GATED_BY → G-EXT-02 for final external completion.

Testing

12.1 TESTED_BY → applicable service testing

12.5 TESTED_BY → density/compaction

12.7 TESTED_BY → concrete testing

12.8 TESTED_BY → asphalt testing

Q. SECTION 13 — TESTING & COMMISSIONING

Now these relationships become much more directional.

Test readiness

13.3 Mechanical Testing GATED_BY → G-TST-01

13.4 Electrical Testing GATED_BY → G-TST-01

13.5 Envelope Testing GATED_BY → G-TST-01

13.6 Functional Testing GATED_BY → G-TST-01

13.7 Equipment Start-Up GATED_BY → G-MEP-02/G-TST-01 as applicable

13.8 Integrated Testing GATED_BY → G-LS-01 or other system-readiness gate

Documentation

13.3 REQUIRES 13.2 Test Documentation

13.4 REQUIRES 13.2

13.5 REQUIRES 13.2

13.6 REQUIRES 13.2

13.7 REQUIRES 13.2

13.8 REQUIRES 13.2

Failure loop

Any test node:

13.3/13.4/13.5/13.6/13.7/13.8

on failure:

→ 13.9 Failed-Test Management

13.10 Retesting REQUIRES 13.9 corrective action complete

13.11 Acceptance Evidence REQUIRES successful applicable testing/retesting

Build 2 requires the original failed result to remain traceable through correction, retest and acceptance.

R. SECTION 14 — CLOSEOUT

Deficiency chain

14.2 Formal Deficiency Survey REQUIRES 14.1 Preparatory Deficiency Review

14.3 Classification REQUIRES 14.2

14.4 Assignment REQUIRES 14.3

14.5 Corrective Work REQUIRES 14.4

14.6 Reinspection REQUIRES 14.5

14.7 Closure REQUIRES 14.6

This is one of our cleanest pure chains.

Testing

14.9 Outstanding Test Results REQUIRES status from 13.x

14.15 Turnover REQUIRES 14.9 sufficiently resolved

Records

14.14 Final Quality Records REQUIRES 14.10 As-Builts

14.14 REQUIRES 14.11 O&M

14.14 REQUIRES 14.12 Certificates

14.14 REQUIRES 14.13 Warranties

14.14 REQUIRES 13.11 Acceptance Evidence

Final turnover

14.15 Turnover REQUIRES 14.7 Deficiency Closure

14.15 REQUIRES 14.8 NC Closure

14.15 REQUIRES 14.9 Test Closure

14.15 REQUIRES 14.14 Final Quality Records

14.15 GATED_BY → G-FINAL-01

Build 2 explicitly defines turnover as the final project-quality gate.

S. GLOBAL INHERITED RELATIONSHIPS

This part drastically reduces our graph size.

Every inspection-capable activity automatically inherits:

Issue

Deficiency found → Section 14 deficiency workflow

No repeated edge required.

NC

Condition qualifies as NC → NC process → 14.8 Outstanding NC Closure

No repeated edge.

Evidence

Every node can produce evidence.

Reporting

Every node retains its reporting/analysis content from Build 2.

Closeout evidence

Accepted records may ultimately feed 14.14 Final Quality Records.

No need for 100+ explicit EVIDENCE → 14.14 relationships.

T. AS-BUILT RULE

AS_BUILT_FEEDS → 14.10

should be conditional, not permanent.

Activities likely to trigger it include:

- 12.1 Underground Services

- 1.7 Site Drainage

- 8.x service routing

- 9.x service routing

- equipment relocation

- penetrations

- field-approved layout changes.

Rule:

If installed configuration differs from latest record information, create/update as-built impact.

U. RECIPROCAL BEHAVIOR

We now freeze this:

INTERFACES_WITH

Stored once.

Automatically visible from both nodes.

Example:

8.5 INTERFACES_WITH 10.4

renders:

HVAC Ductwork
→ Related: Fire/Smoke Dampers

and:

Fire/Smoke Dampers
→ Related: HVAC Ductwork

No duplicate edge.

REQUIRES

Directional.

Reverse produces After, but does not create a second stored relationship.

TESTED_BY

Directional.

Test page automatically knows its tested systems from reverse lookup.

ACCESS_CHECKED_BY

Directional, but 11.10 can automatically list all incoming access-controlled activities.

V. CONDITION MODEL

Some relationships need contextual conditions.

We should allow:

always

whereApplicable

whereRated

whereExterior

whereConcealed

whereSpecified

whereEquipmentPresent

whereTestingRequired

whereFireSeparation

Examples:

8.9 INTERFACES_WITH 10.3
condition: whereFireSeparation

8.9 INTERFACES_WITH 4.2
condition: whereExterior

3.5 TESTED_BY NDT
condition: whereSpecified

This is extremely important for a universal guide because we cannot pretend every building uses every system.

W. STEP 2 OUTPUT — CANONICAL EDGE FORMAT

This is basically what Codex will eventually consume:

Relationship {

sourceId

type

targetId

strength

condition

notes?

}

For symmetric edges:

type = INTERFACES_WITH

the app knows reciprocity automatically.

For dependencies:

source = downstream node

type = REQUIRES

target = prerequisite

Always the same orientation.

That convention is critical.

X. BUILD 3 STEP 2 — FROZEN RULES

We can now freeze:

Canonical stored relationship types ✓

Dependency orientation ✓

Automatic Before/After derivation ✓

Automatic interface reciprocity ✓

Hard / conditional / coordination strength ✓

Context conditions ✓

Universal deficiency inheritance ✓

Universal NC inheritance ✓

Universal evidence behavior ✓

Conditional as-built behavior ✓

Cross-discipline hub behavior ✓

Section 1–14 relationship registry ✓

The next Step 3 should therefore not revisit these links.

Step 3 becomes much more focused:

Directionality & reciprocal-display rules

but because we've already established most of that while normalizing Step 2, Step 3 can be short and precise: essentially the rules determining exactly how the UI converts these stored relationships into Before, After, Interfaces, Related QC, Testing and navigation-back behavior.

That is where the graph turns into navigation.

Yes. Step 3 should be short, formal, and implementation-oriented. Step 2 already did the conceptual work; Step 3 freezes exactly how those relationships behave in navigation.

BUILD 3 — STEP 3

DIRECTIONALITY & RECIPROCAL-DISPLAY RULES

The core principle is:

We store each relationship once, then derive the user-facing navigation from it.

That prevents duplicated links, inconsistent navigation, and unnecessary maintenance.

1. REQUIRES

Stored direction

Always:

Downstream activity → prerequisite

Example:

2.5 Foundation Concrete REQUIRES 2.4 Pre-Pour Quality Gate

Display on 2.5

Before

- 2.4 Pre-Pour Quality Gate

Display on 2.4

After

- 2.5 Foundation Concrete

Rule

REQUIRES is not reciprocal.

The reverse relationship exists only as a derived navigation view.

So we never separately store:

2.4 NEXT 2.5

because it is redundant.

UI mapping

| Stored edge | Source page | Target page |
| --- | --- | --- |
| A REQUIRES B | Before: B | After: A |

2. INTERFACES_WITH

Stored direction

Direction is irrelevant.

Example:

8.5 HVAC Ductwork INTERFACES_WITH 10.4 Fire/Smoke Dampers

Display on 8.5

Interfaces

- Fire / Smoke Dampers

Display on 10.4

Interfaces

- HVAC Ductwork

Rule

Automatically reciprocal.

Store only one edge.

Never:

8.5 ↔ 10.4

plus another separate record:

10.4 ↔ 8.5

3. GATED_BY

Stored direction

Activity being controlled → gate

Example:

6.4 Gypsum Board GATED_BY G-INT-01

Display on 6.4

Required Gate

- Interior Wall / Ceiling Pre-Concealment Gate

Display on G-INT-01

Controls

- Gypsum Board

- Ceilings

- any other incoming activities

Rule

Directional, but the gate automatically sees all incoming activities.

UI mapping

Activity:

Gate / Release Requirement

Gate:

Activities Controlled

4. TESTED_BY

Stored direction

Construction/system activity → test activity

Example:

4.8 Windows / Glazing TESTED_BY 13.5 Building Envelope Testing

Display on 4.8

Testing

- Building Envelope Testing

Display on 13.5

Applies To

- Windows / Glazing

- Exterior Wall Assemblies

- Roofing where applicable

- etc.

Rule

Directional relation, reciprocal discovery.

Testing pages can automatically list all incoming tested systems.

5. COMMISSIONED_BY

Same behavior as TESTED_BY, but displayed separately.

Example:

8.6 HVAC Equipment COMMISSIONED_BY 13.7 Equipment Start-Up

HVAC Equipment page

Commissioning

- Equipment Start-Up

- Functional Testing where applicable

Equipment Start-Up page

Equipment / Systems

- HVAC Equipment

- Electrical equipment where applicable

- etc.

We should keep Testing and Commissioning visually distinct even though both are verification activities.

6. PENETRATION_MANAGED_BY

Stored direction

Specific penetration activity → universal penetration hub

Example:

8.9 Mechanical Penetrations PENETRATION_MANAGED_BY 11.7 Universal Penetrations

Display on 8.9

Universal Workflow

- Universal Penetrations

Display on 11.7

Specific Penetration Types

- Mechanical Penetrations

- Electrical Penetrations

- Roof Penetrations

- Firestopping interfaces

This creates the useful relationship:

specific technical page ↔ universal multidisciplinary workflow

without duplicating the content.

7. ACCESS_CHECKED_BY

Stored direction

Equipment/system → 11.10 Access & Maintainability

Example:

10.4 Fire/Smoke Dampers ACCESS_CHECKED_BY 11.10

Damper page

Access & Maintainability

- Verify access after completion

11.10 page

Applies To

- Dampers

- HVAC equipment

- electrical equipment

- valves

- controls

- access panels

- etc.

Again, one stored edge.

8. CLOSES_THROUGH

Stored direction

Technical activity → relevant closeout process

Example:

7.7 Final Architectural Deficiency Inspection CLOSES_THROUGH 14.2 Formal Deficiency Survey

Technical page

Closeout

- Formal Deficiency Survey

Closeout page

Related Completion Streams

- Architectural

- Mechanical

- Electrical

- External

- etc.

This should generally appear lower on the page because it matters later in the lifecycle.

9. AS_BUILT_FEEDS

Stored direction

Activity → 14.10 Redlines / As-Builts

But its visibility should be conditional.

Example:

12.1 Underground Services AS_BUILT_FEEDS 14.10

Display

Normally:

As-Built Impact

Then either:

Potential

or if actual field change exists later:

Required

For the universal guide, we only need the relationship showing:

“This type of work may affect final record drawings.”

We are not tracking actual project redlines in the MVP.

10. PRE-CONCEALMENT IS NOT A RELATIONSHIP

We freeze this now.

preConcealment is a node characteristic.

Example:

10.3 Firestopping

has:

preConcealment = true

Therefore the app can automatically surface it under:

Before Concealment

without storing a special link.

This makes filtering much simpler.

11. HIGH CONTROL IS ALSO NOT A RELATIONSHIP

Same principle.

These are metadata:

- highControl

- traceabilityCritical

- specialistInterface

- preConcealment

They affect:

- visual warnings;

- filtering;

- Quick mode;

- Learn mode;

- “Don't Miss” content;

but not graph direction.

12. CONDITIONS CONTROL VISIBILITY

Relationships can exist universally but only appear when their condition is relevant.

Example:

8.9 Mechanical Penetrations INTERFACES_WITH 10.3 Firestopping

Condition:

whereFireSeparation

Therefore the interface could display:

Firestopping — where penetrating a rated assembly

rather than implying that every mechanical penetration needs firestop.

Likewise:

8.9 ↔ 4.2 Air Barrier

condition:

whereExteriorEnvelope

This is essential.

13. CONDITION DISPLAY RULE

Conditions should not look like programming logic to the field user.

Stored:

whereFireSeparation

Displayed:

Firestopping — if penetration passes through a fire-rated assembly

Stored:

whereExterior

Displayed:

Air / Water Control — if penetration crosses the exterior envelope

Stored:

whereSpecified

Displayed:

Testing — where required by project documents

14. HARD VS CONDITIONAL RELATIONSHIPS

This affects the visual presentation.

hard

A real prerequisite.

Display prominently:

BEFORE YOU PROCEED

Example:

Pre-Pour Quality Gate

conditional

Display with qualifier:

CHECK IF APPLICABLE

Example:

Firestopping — where rated

coordination

Display under:

INTERFACES / COORDINATION

rather than making it look like a blocker.

This prevents the guide from making every related issue look equally critical.

15. PAGE NAVIGATION ORDER

Every activity page should derive its navigation in the same order.

I would freeze:

1. BEFORE

Derived from outgoing REQUIRES.

2. GATES

Derived from GATED_BY.

3. INTERFACES

Derived from INTERFACES_WITH.

4. UNIVERSAL WORKFLOWS

For PENETRATION_MANAGED_BY, ACCESS_CHECKED_BY, etc.

5. TESTING

Derived from TESTED_BY.

6. COMMISSIONING

Derived from COMMISSIONED_BY.

7. AFTER

Reverse lookup of incoming REQUIRES.

8. CLOSEOUT

Derived from CLOSES_THROUGH / AS_BUILT_FEEDS.

That gives a natural field logic:

What must be ready? → What gate matters? → What touches this? → What universal control applies? → How is it tested? → What happens next?

16. “RELATED QC” SHOULD BE DERIVED, NOT MANUALLY CURATED

This is important.

We should not create another manually maintained list called Related QC.

The app generates it from:

- Interfaces

- Universal workflows

- Testing

- Commissioning

- Gates

- Closeout

Otherwise we'd end up maintaining the same relationship twice.

If needed, the UI can simply show:

Related QC

and combine those relationship types.

But the database doesn't need a RELATED_QC edge.

17. PARENT / CHILD NAVIGATION

This is different from cross-link relationships.

Example:

8 Mechanical Services

→ 8.5 HVAC Ductwork

That is hierarchy, not a relationship edge.

So every activity has:

parentSectionId

Example:

8.5.parentSectionId = 8

UI:

Mechanical Services → HVAC Ductwork

We should not store:

8.5 REQUIRES 8

or anything similar.

18. BREADCRUMB RULES

There are actually two types of navigation history.

Hierarchical breadcrumb

Shows where the page belongs.

Example:

Mechanical Services > Mechanical Penetrations

If you cross-link into Firestopping:

Fire & Life Safety > Firestopping

This breadcrumb always reflects canonical hierarchy.

Navigation history

Separately, the browser/app remembers how you arrived.

Example:

You go:

Mechanical Penetrations
→ Firestopping

The Firestopping page says canonically:

Fire & Life Safety > Firestopping

but Back returns to:

Mechanical Penetrations

This avoids producing nonsense breadcrumbs like:

Mechanical > Mechanical Penetrations > Firestopping

because Firestopping doesn't actually live under Mechanical.

That distinction is important.

19. CROSS-LINK OPENING BEHAVIOR

When tapping a cross-link:

- stay in same tab/view;

- navigate directly to destination;

- preserve navigation stack;

- scroll destination page to top;

- optionally highlight why you arrived there.

Example:

From Mechanical Penetrations tap:

Firestopping

The destination could briefly show:

Related from: Mechanical Penetrations

That would help orientation.

Not necessary for MVP, but useful.

20. BACK BUTTON BEHAVIOR

Priority:

1.

Return to previous actual navigation location.

2.

If no navigation history exists, return to canonical parent.

This gives predictable behavior whether you entered via search, hierarchy, favorites, or cross-link.

21. SEARCH ENTRY BEHAVIOR

If user searches:

firestop

and enters 10.3 directly:

There is no prior activity context.

Therefore:

Back → Search Results

If opened from home search directly and search results aren't preserved:

Back → previous screen

Canonical breadcrumb remains:

Fire & Life Safety > Firestopping

22. RECIPROCAL INTERFACE SORTING

When a page has many interfaces, sort them meaningfully rather than alphabetically.

Recommended order:

- Critical / high-control

- Pre-concealment

- Structural

- Envelope

- Mechanical

- Electrical

- Fire/Life Safety

- Architectural

- Testing/commissioning

- Others

We can refine the exact UI order later in Build 5.

23. DUPLICATE LINK SUPPRESSION

Suppose 8.9 Mechanical Penetrations has:

- INTERFACES_WITH 10.3 Firestopping

- PENETRATION_MANAGED_BY 11.7

- and 11.7 itself links to 10.3.

The page should not repeat Firestopping three times.

Rule:

direct relationship outranks indirect relationship.

Display:

Interfaces

- Firestopping

Universal Workflow

- Universal Penetrations

That's enough.

24. INDIRECT RELATIONSHIPS

For MVP, I recommend:

Only show direct edges by default.

Don't automatically show:

“Related because a related page is related to another page.”

Otherwise the graph explodes.

Example:

HVAC Equipment ↔ BAS ↔ Electrical Distribution

HVAC Equipment should only show Electrical Distribution if we deliberately created a direct interface edge.

No automatic second-degree network display.

Search can find everything else.

25. SECTION 11 HUB BEHAVIOR

The multidisciplinary section is special.

When entering:

11.4 Envelope ↔ Mechanical

the page should show both sides:

Envelope

- Air Barrier

- Vapour Barrier

- Insulation

- Roof

- Sealants

Mechanical

- Piping

- Ductwork

- Equipment

- Penetrations

But this does not mean every individual pair is stored.

Section 11 can use its hub definitions from Step 2.

That keeps the edge registry manageable.

26. SECTION 13 TEST PAGE BEHAVIOR

Test pages reverse-index incoming systems.

Example:

13.5 Building Envelope Testing

Related Systems

- Exterior Wall Assemblies

- Windows

- Exterior Doors where required

- Roofing Testing

- applicable penetrations/interfaces

Then:

Before

- Test Readiness

- Test Documentation

If Fail

- Failed-Test Management

After Pass

- Acceptance Evidence

This makes Section 13 feel like a testing workflow rather than another construction trade.

27. SECTION 14 CLOSEOUT PAGE BEHAVIOR

Similarly, closeout pages emphasize lifecycle rather than technical interfaces.

Example:

14.6 Reinspection

Before

- Corrective Work

After

- Closure

If rejected

- return to Corrective Work

This is one case where workflow branching matters.

We'll formalize state transitions later.

28. ONE-WAY VS TWO-WAY — FINAL TABLE

| Relationship | Stored Once | Reciprocal Display | Reverse Derived |
| --- | --- | --- | --- |
| REQUIRES | ✓ | No | After |
| INTERFACES_WITH | ✓ | Yes | — |
| GATED_BY | ✓ | Gate sees controlled activities | — |
| TESTED_BY | ✓ | Test sees tested activities | — |
| COMMISSIONED_BY | ✓ | Commissioning page sees systems | — |
| PENETRATION_MANAGED_BY | ✓ | Hub sees penetration types | — |
| ACCESS_CHECKED_BY | ✓ | Hub sees applicable assets | — |
| CLOSES_THROUGH | ✓ | Closeout sees incoming streams | — |
| AS_BUILT_FEEDS | ✓ | As-built page sees applicable activities | — |

29. USER-FACING NAVIGATION LABELS

Internally:

REQUIRES

User sees:

Before

Internally:

reverse REQUIRES

User sees:

After

Internally:

INTERFACES_WITH

User sees:

Interfaces

Internally:

TESTED_BY

User sees:

Testing

Internally:

COMMISSIONED_BY

User sees:

Commissioning

Internally:

GATED_BY

User sees:

Gate / Before Proceeding

Internally:

PENETRATION_MANAGED_BY

User sees:

Universal Penetration Workflow

Internally:

ACCESS_CHECKED_BY

User sees:

Access & Maintainability

Internally:

CLOSES_THROUGH

User sees:

Closeout

This separation means Build 4 can later translate user-facing labels without changing the graph.

30. STEP 3 — FROZEN NAVIGATION MODEL

We now have:

Canonical directionality rules ✓

Before derived from outgoing prerequisites ✓

After derived from reverse prerequisite lookup ✓

Interfaces reciprocal automatically ✓

Tests reverse-index their systems ✓

Commissioning reverse-indexes systems ✓

Gate pages reverse-index controlled activities ✓

Conditional relationships displayed contextually ✓

Direct links prioritized over indirect links ✓

No second-degree graph clutter ✓

Canonical breadcrumb separated from navigation history ✓

Back behavior defined ✓

Section 11 hub behavior defined ✓

Section 13 testing behavior defined ✓

Section 14 workflow behavior defined ✓

Database relationship names separated from UI labels ✓

And most importantly:

We now know exactly how one stored edge becomes the navigation that you see in the field.

So Step 3 is complete.

Step 4 should be the Gate Registry. That's where we stop speaking generally about “pre-concealment” and formally define every universal gate—its inputs, blocking conditions, release conditions, and what downstream work it controls. That will be especially important for the future “Before Closing / Before Pour / Before Backfill / Ready to Test” field shortcuts.

Good. Step 4 is the Gate Registry, and this is where we formalize exactly what each universal gate means, what feeds it, what blocks it, and what it releases.

We should keep this tight and universal. The gates are not CRT/Hochelaga hold points. They are field-reference decision gates in our guide. Actual project hold/witness/release requirements still come from the real project documents.

The Build 2 source supports that approach strongly. Its pre-pour logic explicitly says concrete should not proceed until prerequisite quality conditions are satisfied or formally released, and it defines the required document, formwork, reinforcement, embed, site-condition, testing, communication and deficiency checks.

BUILD 3 — STEP 4

CANONICAL GATE REGISTRY

I would freeze 11 universal gates.

Each gate gets these fields:

| Field | Meaning |
| --- | --- |
| Gate ID | Immutable logic-node ID |
| Gate Name | Canonical English name |
| Purpose | What progression decision it controls |
| Inputs | Activities/information feeding the gate |
| Blocking Conditions | Conditions preventing release |
| Release Conditions | What must be true to proceed |
| Controls | Downstream work affected |
| Reopen / Invalidate Trigger | What can invalidate a released gate |
| Severity | Hard / Conditional |

G-STR-01 — STRUCTURAL PRE-POUR GATE

Purpose

Prevent concrete placement until all relevant formwork, reinforcement, embeds, openings, conditions, testing preparation and releases are acceptable.

Build 2 expressly gives this as a standalone quality system.

Inputs

Core

- 2.1 Foundation Formwork

- 2.2 Foundation Reinforcement

- 2.3 Embedded Items

Cross-discipline where applicable

- 9.1 Embedded conduits

- 9.6 Grounding/bonding components

- 11.8 Embedded Items

- mechanical sleeves/openings

- anchor bolts

- plates/inserts

- waterstops

- blockouts

- survey/layout

Required checks

Documents

- latest drawings;

- current shop drawings;

- technical changes;

- PIE/PRIE;

- approved mix;

- required procedures.

Formwork

- dimensions;

- elevation;

- alignment;

- stability;

- cleanliness;

- openings/joints.

Reinforcement

- size;

- quantity;

- spacing;

- cover;

- laps;

- anchorage;

- stability.

Embeds

- anchors;

- sleeves;

- inserts;

- conduits;

- plates;

- waterstops;

- openings.

Site

- accepted base/substrate;

- water/debris removed;

- access;

- weather controls.

Testing

- required laboratory/testing arrangements ready.

Build 2 lists these items directly.

Blocking conditions

🔴 Any unresolved critical formwork issue
🔴 Incorrect/missing reinforcement
🔴 Missing/mislocated embed
🔴 Unresolved MEP clash
🔴 Base/substrate not accepted
🔴 Required inspection not complete
🔴 Required hold/witness/release missing
🔴 Testing arrangements not ready
🔴 Open deficiency that would be permanently concealed

Release condition

POUR READY

Build 2 uses exactly that completion logic.

Controls

- 2.5 Foundation Concrete

- 3.1 Cast-in-Place Concrete

- 2.8 Slab-on-Grade

- 12.7 Exterior Concrete where applicable

Reopen / invalidate

- rebar moved;

- formwork altered;

- embed added/moved;

- conduit/sleeve changed;

- new clash;

- weather/site condition materially changes before pour.

Severity

HARD

G-ENV-01 — ENVELOPE PRE-CONCEALMENT GATE

Purpose

Ensure the building-envelope control layers and interfaces are acceptable before subsequent layers make them inaccessible.

Inputs

- 4.2 Air Barrier

- 4.3 Vapour Barrier

- 4.4 Thermal Insulation

- 4.5 Exterior Sheathing

- 4.8 Windows/Glazing

- 4.9 Exterior Doors

- 4.10 Sealants

- 8.9 Mechanical Penetrations

- 9.9 Electrical Penetrations

- 11.4 Envelope ↔ Mechanical

- 11.5 Envelope ↔ Electrical

Required checks

Substrate

- acceptable;

- dry/clean where required;

- repaired.

Control layers

- correct product;

- continuous;

- seams/laps complete;

- transitions complete.

Openings

- sill/head/jamb integration;

- anchorage;

- air/water transition.

Penetrations

- coordinated;

- membrane restored;

- insulation continuity restored;

- flashing/seal complete.

Evidence

- concealed interfaces photographed;

- deficiencies corrected.

Blocking conditions

🔴 Tear/discontinuity in air/water control layer
🔴 Unsealed penetration
🔴 Wet/damaged insulation
🔴 Window/door transition incomplete
🔴 Flashing incomplete
🔴 Unresolved envelope deficiency about to be concealed

Release condition

ENVELOPE LAYER READY FOR COVERING / NEXT ASSEMBLY LAYER

Controls

- cladding;

- exterior masonry;

- further insulation;

- interior closure where vapour control involved;

- finish work.

Reopen / invalidate

- later MEP penetration;

- membrane damage by another trade;

- window/door replacement;

- removed flashing;

- field modification.

Severity

HARD where concealment occurs; CONDITIONAL otherwise

G-ROOF-01 — ROOF ASSEMBLY PROGRESSION GATE

Roofing needs slightly different treatment because Build 2 establishes five successive inspection windows, not one single checkpoint.

So G-ROOF-01 should actually contain five sub-gates.

G-ROOF-01A — Before Air/Vapour Layer

Inputs:

- 5.1 Roof Deck/Substrate

- openings

- curbs

- drains

Release requires:

- deck accepted;

- openings/curbs correct;

- drains coordinated;

- surface clean/dry.

Controls:

- 5.2 Vapour/Air Control Layer

G-ROOF-01B — Before Insulation

Inputs:

- 5.2 Vapour/Air Control Layer

Release requires:

- membrane continuous;

- seams complete;

- penetrations sealed;

- wall/parapet transitions complete;

- repairs closed.

Controls:

- 5.3 Roof Insulation

G-ROOF-01C — Before Roofing Membrane

Inputs:

- 5.3 Roof Insulation

Release requires:

- correct insulation;

- thickness;

- taper/slope;

- fastening;

- no wet boards;

- drain sumps correct.

Controls:

- 5.4 Roofing Membrane

G-ROOF-01D — Before Equipment / Traffic Obscures Final Membrane

Inputs:

- 5.4 Membrane

- 5.5 Flashings

- 5.6 Penetrations

- 5.7 Curbs

- 5.8 Drains

Release requires:

- membrane complete;

- seams accepted;

- flashings complete;

- penetrations complete;

- curbs complete;

- drains complete.

Controls:

- rooftop equipment installation;

- later roof traffic/obscuration.

G-ROOF-01E — Final Roof Acceptance

Inputs:

- 5.9 Roofing Testing / Final Inspection

Release requires:

- testing complete;

- drainage acceptable;

- deficiencies addressed;

- repairs complete;

- retesting complete;

- warranty documentation complete.

Reopen / invalidate

Any:

- new penetration;

- membrane damage;

- curb modification;

- roof-equipment relocation;

- failed test;

- later leak.

Severity

HARD

G-INT-01 — INTERIOR WALL / CEILING PRE-CONCEALMENT GATE

Purpose

Prevent wall or ceiling closure until concealed architectural, MEP, fire/acoustic and access conditions are acceptable.

Build 2 states that before wall or ceiling closure, the system should force a final review.

Inputs

- 6.1 Interior Masonry where applicable

- 6.2 Metal Stud Framing

- 6.3 Interior Insulation

- 6.5 Fire-Rated Assemblies

- 6.9 Access Panels

- 8.x MEP rough-ins

- 9.x electrical rough-ins

- 10.3 Firestopping

- 10.4 Dampers

- 11.6 Architectural ↔ MEP

Required checks

Documents

- wall/ceiling type;

- MEP drawings;

- fire/life-safety details;

- technical changes.

Framing / masonry

- layout;

- openings;

- backing;

- reinforcement;

- anchors/support.

MEP

- rough-in complete;

- required tests complete;

- boxes/sleeves correct;

- services supported;

- no unresolved clashes.

Fire / acoustic

- correct rated assembly;

- firestop complete;

- acoustic insulation;

- head-of-wall;

- rated openings coordinated.

Access

- valves accessible;

- dampers accessible;

- junction boxes/access items addressed;

- access panels identified.

Evidence

- photographs;

- inspection records;

- test records;

- deficiencies corrected;

- release obtained where required.

Build 2 gives these checks explicitly.

Blocking conditions

🔴 Rough-in incomplete
🔴 Required test incomplete/failed
🔴 Missing backing
🔴 Firestop incomplete
🔴 Damper inaccessible
🔴 Valve/junction box becoming inaccessible
🔴 Open clash
🔴 Rated assembly incomplete
🔴 Required evidence missing

Release

WALL / CEILING READY TO CLOSE

Controls

- 6.4 Gypsum Board

- 6.8 Ceilings

- relevant shaft/enclosure closure

Reopen / invalidate

- new MEP penetration;

- added device;

- firestop disturbed;

- service rerouted;

- access requirement introduced;

- wall assembly modified.

Severity

HARD

G-MEP-01 — MEP PRE-CONCEALMENT GATE

This overlaps deliberately with G-INT-01, but the purpose is different.

G-INT-01 asks:

Can the wall/ceiling close?

G-MEP-01 asks:

Is the concealed MEP work itself ready to disappear?

That distinction is valuable.

Inputs

- 8.1–8.5 installed systems

- 8.9 Mechanical Penetrations

- 8.10 Mechanical Testing

- 9.1 Raceways

- 9.2 Cable Trays as applicable

- 9.3 Supports

- 9.6 Grounding/Bonding

- 9.9 Electrical Penetrations

- firestop/dampers where affected

- access requirements

Release requires

☐ route/location acceptable
☐ supports complete
☐ penetrations/interfaces complete
☐ required mechanical tests passed
☐ concealed electrical work inspected/documented
☐ firestop complete
☐ dampers/access addressed
☐ insulation complete where required
☐ evidence captured
☐ unresolved deficiencies controlled

Controls

- insulation;

- drywall closure;

- ceiling closure;

- shaft closure;

- other architectural concealment.

Reopen / invalidate

Any modification to concealed MEP.

Severity

HARD when concealment imminent

G-MEP-02 — EQUIPMENT COMMISSIONING READINESS GATE

Purpose

Determine whether major equipment is actually ready for start-up/commissioning, not merely installed.

Inputs

- 8.6 HVAC Equipment

- 8.8 Controls/BAS

- 9.4 Electrical Equipment Installation

- 9.5 Distribution Interfaces

- 9.6 Grounding/Bonding

- 9.10 Identification

- 11.9 Equipment Bases

- 11.10 Access & Maintainability

- prerequisite mechanical/electrical tests

Required checks

Physical

- correct equipment;

- base/anchors complete;

- clearances;

- vibration isolation where required;

- guards/covers;

- room/environment ready.

Mechanical

- piping connected;

- ductwork connected;

- drains complete;

- valves/interfaces complete.

Electrical

- supply/interface complete;

- grounding/bonding interface complete;

- specialist prerequisites satisfied.

Controls

- sensors/actuators/interfaces installed;

- controls available.

Documentation

- manufacturer start-up procedure;

- required test forms;

- equipment identification.

Blocking conditions

🔴 Incomplete physical installation
🔴 Incomplete service connection
🔴 Failed prerequisite test
🔴 Controls unavailable
🔴 Missing electrical acceptance
🔴 Access/clearance issue
🔴 Missing manufacturer prerequisite
🔴 Open issue affecting safe start-up

Release

READY FOR EQUIPMENT START-UP / COMMISSIONING

Controls

- 13.7 Equipment Start-Up

- 13.6 Functional Testing

Build 2's AHU sequence specifically runs installation → mechanical testing → electrical interface → controls → start-up → functional test → TAB → acceptance evidence.

Severity

HARD

G-LS-01 — LIFE-SAFETY INTEGRATED READINESS GATE

Purpose

Determine whether the individual fire/life-safety components and interfaces are complete enough to undergo integrated testing.

Inputs

- 10.1 Fire-Rated Walls

- 10.2 Fire-Rated Floors/Ceilings

- 10.3 Firestopping

- 10.4 Fire/Smoke Dampers

- 10.5 Fire-Rated Doors

- 10.6 Fire Alarm Physical Interfaces

- 10.8 Fire Protection

- 9.8 Emergency Lighting

- emergency power/interfaces

- architectural egress conditions

Required checks

Rated assemblies

- correct;

- complete;

- concealed elements inspected.

Penetrations

- identified;

- approved firestop system;

- complete;

- documented.

Dampers

- correct;

- installed;

- accessible;

- interfaces complete.

Doors

- rated components complete;

- operation ready.

MEP

- fire-related penetrations complete.

Records

- firestop register;

- photos;

- inspections;

- deficiencies/NCs resolved or formally controlled.

The source makes this one of the strongest STOP/CHECK points in the entire guide.

Blocking conditions

🔴 Incomplete rated assembly
🔴 Missing firestop
🔴 Inaccessible damper
🔴 Fire door not ready
🔴 Fire alarm interface incomplete
🔴 Emergency system not ready
🔴 Open significant life-safety deficiency
🔴 Required component test incomplete

Release

READY FOR LIFE-SAFETY FUNCTIONAL / INTEGRATED TESTING

Controls

- 13.8 Integrated/System Testing

- life-safety final acceptance

Reopen / invalidate

- new penetration through rated construction;

- firestop disturbed;

- damper/door changed;

- fire-alarm logic/device modification;

- failed integrated test.

Severity

HARD

G-EXT-01 — UNDERGROUND / PRE-BACKFILL GATE

Purpose

Prevent burial of underground work until the service, geometry, tests and traceability are complete.

Build 2 explicitly requires inspection, release and no unresolved deficiency before burial.

Inputs

- 12.1 Underground Services

- 12.2 Utility Trenches

- 12.3 Structures

- applicable 8.x underground mechanical

- applicable 9.x underground electrical

- survey/as-built data

Required checks

Excavation

- route;

- bottom elevation;

- acceptable trench/subgrade.

Service

- correct type;

- material/size;

- elevation/slope;

- joints;

- crossings/separations.

Structures

- manholes/catch basins accepted;

- inverts;

- connections.

Testing

- required tests complete;

- failures repaired/retested.

Traceability

- as-built survey;

- photos;

- service ID.

Blocking conditions

🔴 Failed/missing test
🔴 Wrong elevation/slope
🔴 Unaccepted joint/connection
🔴 As-built not captured
🔴 Open deficiency about to be buried
🔴 Missing required release

Release

READY FOR BACKFILL

Controls

- 1.6 Backfill

- 2.12 Backfill Against Structure

- external trench backfill

Reopen / invalidate

Usually not after backfill; later failure creates a new deficiency/NC and may require excavation.

Severity

HARD

G-EXT-02 — EXTERNAL WORKS COMPLETION GATE

Purpose

Determine whether site/external works are complete enough for final acceptance.

Build 2 requires accepted underground utilities/testing/as-builts, compaction/base, drainage, curbs/concrete/asphalt, restoration, fencing where applicable, cleanup and documentation.

Inputs

- 12.1–12.10

- testing

- as-builts

- deficiencies/NC closure

Release requires

Below grade

- utilities accepted;

- testing complete;

- as-builts complete;

- structures complete.

Earthworks

- backfill;

- compaction;

- base/subbase accepted.

Drainage

- grades correct;

- drains functional;

- no unintended ponding.

Surfaces

- curbs;

- concrete;

- asphalt;

- transitions.

Site

- restoration;

- gates/fencing where applicable;

- existing assets restored;

- temporary works removed;

- cleanup.

Documentation

- surveys;

- tests;

- approvals;

- inspections;

- photos;

- issue closure.

Release

EXTERNAL WORKS QUALITY COMPLETE

Controls

- 12.9 final site completion

- 14.x final closeout

Severity

HARD for final external acceptance

G-TST-01 — TEST READINESS GATE

Purpose

Ensure testing begins only when the system is built enough, documentation is correct, and personnel/instruments are ready.

Build 2's master testing flow asks first whether the system is built, then whether it is ready to test.

Inputs

- relevant installation activity

- 13.1 Test Readiness

- 13.2 Test Documentation

- open deficiency status

- test procedure

- calibration/personnel/witness requirements

Required checks

System

- installation complete;

- inspections complete;

- deficiencies controlled.

Procedure

- approved/current.

Utilities

- available.

Instruments

- correct;

- calibration valid.

People

- qualified specialist;

- witnesses as required.

Blocking conditions

🔴 Construction incomplete
🔴 Open issue invalidating result
🔴 No approved procedure
🔴 Missing/expired calibration
🔴 Missing specialist
🔴 Missing required witness
🔴 Unsafe/unavailable test condition

Release

READY TO TEST

Controls

- 13.3

- 13.4

- 13.5

- 13.6

- 13.7 where applicable

- 13.8 where applicable

Reopen / invalidate

- system changed after readiness;

- new deficiency;

- instrument/calibration issue;

- changed test boundary.

Severity

HARD

G-FINAL-01 — FINAL TURNOVER / ACCEPTANCE GATE

Purpose

Determine whether physical work, quality issues, testing, records and owner-readiness requirements have converged sufficiently for turnover.

Build 2 defines the final checkpoint across physical completion, deficiencies/NCRs, testing/commissioning, as-builts/O&M/certificates/warranties, owner readiness and final acceptance.

Inputs

- 14.7 Deficiency Closure

- 14.8 Outstanding NC Closure

- 14.9 Outstanding Test Results

- 14.10 As-Builts

- 14.11 O&M

- 14.12 Certificates/Technical Records

- 14.13 Warranties

- 14.14 Final Quality Records

- 13.11 Acceptance Evidence

Required checks

Physical

- work complete;

- clean;

- no unresolved damage;

- access maintained;

- equipment identified.

Quality

- deficiencies closed;

- NCRs closed;

- corrective actions verified.

Testing

- tests complete;

- failed tests closed;

- retests passed;

- commissioning complete;

- integrated testing complete.

Records

- as-builts;

- O&M;

- certificates;

- technical records;

- warranties;

- inspections;

- test records.

Owner readiness

- training;

- spares;

- keys/access;

- special tools;

- transmittals.

Acceptance

- specialist/professional acceptance where required;

- quality package confirmed;

- client/owner acceptance documented;

- turnover package complete.

Blocking conditions

🔴 Significant/open deficiency
🔴 Open NCR
🔴 Missing/failed test
🔴 Incomplete commissioning
🔴 Missing acceptance evidence
🔴 Missing required as-built/O&M/certificate/warranty
🔴 Required owner-readiness deliverable incomplete
🔴 Formal acceptance dependency incomplete

Release

READY FOR TURNOVER / ACCEPTANCE

Build 2's closeout master sequence moves from internal review through formal survey, correction, reinspection, NC/testing closure, record documents, turnover documentation, final quality dossier and finally turnover/acceptance.

Severity

HARD

One gate I would NOT create separately

Earlier we had both:

- G-INT-01 Interior Wall/Ceiling Pre-Concealment

- G-MEP-01 MEP Pre-Concealment

I would keep both, because they answer different questions.

But I would not create a separate generic “Fire/Life Safety Pre-Concealment Gate” ID in addition to G-LS-01.

Instead:

- fire-rated concealment is handled by G-INT-01 plus high-control nodes 10.1–10.4;

- integrated fire/life-safety readiness is handled by G-LS-01.

That avoids gate proliferation.

Likewise, I would not create separate gates for every test type. G-TST-01 handles generic readiness; the specific test module supplies the technical requirements.

GATE SEVERITY MODEL

We should freeze three gate classes.

| Gate Class | Meaning |
| --- | --- |
| HARD | Guide says downstream work should not proceed until gate is satisfied/released under governing project procedure |
| CONDITIONAL HARD | Hard only when that system/condition applies |
| ADVISORY | Quality review point but not inherently blocking |

Our canonical gates:

| Gate | Class |
| --- | --- |
| G-STR-01 | HARD |
| G-ENV-01 | CONDITIONAL HARD |
| G-ROOF-01A–E | HARD |
| G-INT-01 | HARD |
| G-MEP-01 | CONDITIONAL HARD |
| G-MEP-02 | HARD |
| G-LS-01 | HARD |
| G-EXT-01 | HARD |
| G-EXT-02 | HARD for completion |
| G-TST-01 | HARD |
| G-FINAL-01 | HARD |

Again, “HARD” means inside our universal guide's workflow. It does not grant the guide authority to impose contractual hold points.

GATE STATUS MODEL

This matters for Build 5.

Every gate can use only five simple states:

⚪ NOT REVIEWED

Gate not assessed.

🟡 IN REVIEW

Prerequisites being checked.

🔴 NOT READY

One or more blocking conditions exist.

🔵 AWAITING EXTERNAL / SPECIALIST RELEASE

Everything within inspector control may be complete, but required authorized acceptance is outstanding.

🟢 READY / RELEASED

Applicable gate conditions satisfied according to governing project requirements.

I would not create 15 gate statuses.

Five is enough.

GATE INVALIDATION RULE

This is important enough to freeze now.

A gate marked 🟢 does not necessarily remain green forever.

If later work changes a condition that contributed to the release:

Gate may be reopened automatically or flagged for re-review.

Examples:

G-STR-01

- conduit moved after pre-pour inspection → reopen.

G-ENV-01

- later penetration tears air barrier → reopen affected interface.

G-ROOF-01D

- electrician drills through accepted roof membrane → reopen affected roof area.

G-INT-01

- new cable penetrates rated wall before closure → reopen.

G-LS-01

- firestop modified → integrated readiness affected.

G-TST-01

- equipment modified after test-readiness walkdown → readiness invalidated.

G-FINAL-01

- unresolved test/deficiency discovered → turnover readiness drops.

This is where our earlier INVALIDATES concept becomes useful.

GATE SCOPE RULE

Gate release should apply to a scope, not magically to the entire project.

Examples:

- footing F-04;

- Wall W-203;

- Ceiling Zone C;

- Roof Zone R2;

- underground service segment;

- AHU-01;

- system/area.

Even though the MVP is only a guide and may not track project instances yet, the conceptual gate must be scope-aware.

Otherwise a user could interpret:

“Roof gate passed”

as meaning the entire roof.

The universal content should therefore phrase it as:

For the area/system being reviewed...

FINAL CANONICAL GATE STRUCTURE

So Codex eventually gets something conceptually like:

Gate {

id

name

class

purpose

inputs[]

checks[]

blockingConditions[]

releaseCondition

controls[]

invalidationTriggers[]

}

And the activity relationship graph simply says:

6.4 GATED_BY G-INT-01

The gate object owns the logic.

That is much cleaner than embedding gate logic independently inside Gypsum Board, Ceilings, Mechanical, Electrical, Firestop, etc.

STEP 4 — FROZEN

Gate namespace ✓

11 canonical gate families ✓

Roof sub-gates A–E ✓

Inputs ✓

Blocking conditions ✓

Release conditions ✓

Controlled downstream activities ✓

Invalidation triggers ✓

Hard / Conditional Hard distinction ✓

Five-state gate model ✓

Scope-aware release rule ✓

No project-specific hold-point invention ✓

And importantly, we now have something that will later power extremely useful field shortcuts:

Before Pour
Before Covering Envelope
Before Roof Layer
Before Closing Wall/Ceiling
Before Concealing MEP
Ready to Start Equipment?
Before Backfill
Ready to Test?
Ready for Life-Safety Test?
Ready for Turnover?

That is exactly where Build 3 begins becoming a practical inspector's navigation system rather than merely a relationship database.

Step 5 is the Global Status Model — defining what activity status means across inspection, deficiencies, NCs, testing, correction, acceptance and closure, and which transitions are legally/logically allowed inside our guide.

Yes. Step 5 is the Global Status Model.

The main thing to avoid is one giant status list applied blindly to everything. A concrete inspection, a failed test, a deficiency, a gate, and final turnover do not mean the same thing when they say “open” or “complete.”

So I recommend:

One common status philosophy + a few controlled status families.

That gives consistency without flattening different workflows into nonsense.

Build 2 supports that distinction very clearly. For deficiencies, it separates contractor “done” from verified “closed”; for testing, it requires the full chain FAIL → correction → retest → pass → acceptance; and for overall acceptance it distinguishes physical completion, testing, commissioning, records, and final turnover readiness.

BUILD 3 — STEP 5

GLOBAL STATUS MODEL

1. Core philosophy

Across the entire guide, statuses should answer one of five questions:

Has this been looked at?
Is it ready?
Is there a problem?
Has the problem been corrected and verified?
Has the work/system been accepted/closed?

Those meanings stay universal.

The exact labels vary slightly according to object type.

2. GLOBAL STATUS FAMILIES

I recommend six families:

| Family | Applies To |
| --- | --- |
| Activity Status | Construction/QC activity |
| Gate Status | G-* readiness gates |
| Issue Status | Deficiencies |
| NC Status | Formal non-conformance |
| Test Status | Testing / failed test / retest |
| Acceptance Status | System/area/turnover readiness |

This is enough.

We should not create separate status models for concrete, roofing, mechanical, electrical, firestop, etc.

3. ACTIVITY STATUS

This applies to things like:

- 2.2 Foundation Reinforcement

- 4.2 Air Barrier

- 8.5 HVAC Ductwork

- 10.3 Firestopping

Canonical states

⚪ NOT_STARTED

No review/activity has begun.

Display:

Not Started

🔵 IN_PROGRESS

Work and/or inspection is underway but not ready for final disposition.

Display:

In Progress

🟡 READY_FOR_REVIEW

The work is reported sufficiently complete and awaits quality review.

Display:

Ready for Review

This is useful because:

contractor/subcontractor says finished

is not

QC accepted.

Build 2 repeatedly draws that distinction during reinspection and closure.

🔴 ISSUE_OPEN

An observed deficiency, NC, failed prerequisite or blocking concern prevents normal acceptance.

Display:

Issue Open

This is a summary status. The actual issue lives in the deficiency/NC/test workflow.

🔵 AWAITING_EXTERNAL_ACCEPTANCE

Physical QC within the inspector's scope may be satisfactory, but required specialist/professional/client acceptance remains outstanding.

Display:

Awaiting Specialist / External Acceptance

Very important for:

- electrical;

- fire alarm;

- NDT;

- commissioning;

- engineered repairs.

🟢 ACCEPTED

Applicable inspection requirements have been satisfactorily verified.

Display:

Accepted

But:

Accepted ≠ permanently closed forever.

It may be invalidated by later work.

⚫ NOT_APPLICABLE

Activity does not apply to the particular condition.

Display:

N/A

Because the guide is universal, we absolutely need this.

4. ACTIVITY TRANSITIONS

Normal path:

NOT_STARTED

↓

IN_PROGRESS

↓

READY_FOR_REVIEW

↓

ACCEPTED

If issue:

READY_FOR_REVIEW

↓

ISSUE_OPEN

↓ correction

READY_FOR_REVIEW

↓

ACCEPTED

If specialist needed:

READY_FOR_REVIEW

↓

AWAITING_EXTERNAL_ACCEPTANCE

↓

ACCEPTED

And later:

ACCEPTED

↓ invalidating modification

IN_PROGRESS or ISSUE_OPEN

depending on what happened.

5. GATE STATUS

We essentially established this in Step 4. Now we integrate it into the global system.

Canonical states

⚪ NOT_REVIEWED

Gate hasn't been assessed.

🟡 IN_REVIEW

Prerequisites are being checked.

🔴 NOT_READY

One or more blocking conditions exist.

🔵 AWAITING_RELEASE

Quality prerequisites may be satisfactory, but an authorized project release/witness/specialist step remains outstanding.

🟢 READY_RELEASED

Applicable conditions have been satisfied/released.

These five are enough.

6. GATE TRANSITIONS

NOT_REVIEWED

↓

IN_REVIEW

Then:

All good internally + no external release required

→ READY_RELEASED

or:

Blocking condition

→ NOT_READY

or:

Need authorized release

→ AWAITING_RELEASE

then:

→ READY_RELEASED

If later invalidated:

READY_RELEASED

→ IN_REVIEW or NOT_READY

This is essential for dynamic conditions such as new penetrations or moved embeds.

7. DEFICIENCY / ISSUE STATUS

Build 2 gives us a very clear lifecycle:

identify → classify → assign → correct → reinspect → close.

It also explicitly tracks items as open, ready for reinspection, closed, overdue.

I would formalize that as:

🔴 OPEN

Deficiency identified.

🟠 ASSIGNED

Responsible party established.

🟡 CORRECTION_IN_PROGRESS

Corrective work underway.

🔵 READY_FOR_REINSPECTION

Responsible party indicates correction complete and quality verification is now required.

Build 2 specifically monitors whether an item is corrected and ready for reinspection.

🟣 REINSPECTION_FAILED

Correction inspected but still unacceptable.

This returns the item to correction.

🟢 CLOSED

Actual compliance physically verified and required evidence complete.

Build 2 gives the rule perfectly:

“Done” is contractor status. “Closed” is verified quality status.

8. DEFICIENCY TRANSITION

OPEN

↓

ASSIGNED

↓

CORRECTION_IN_PROGRESS

↓

READY_FOR_REINSPECTION

↓

REINSPECTION

If pass:

CLOSED

If fail:

REINSPECTION_FAILED

↓

CORRECTION_IN_PROGRESS

Build 2 expressly says insufficient correction should be REJECT / REOPEN and remain traceable to the original item rather than casually creating a new deficiency.

9. OVERDUE SHOULD NOT BE A STATUS

Important normalization decision.

An item can be:

ASSIGNED + OVERDUE

or

CORRECTION_IN_PROGRESS + OVERDUE

Therefore:

overdue = true/false

should be a flag, not a mutually exclusive status.

Likewise:

- priority;

- turnover-blocking;

- high-risk;

are flags/attributes.

This keeps status logic clean.

10. NC STATUS

NCs deserve their own lifecycle because they can require formal disposition and technical/professional acceptance.

Build 2 says every formal NC must reach an approved disposition, corrective action, verification and documented closure.

I recommend:

🔴 NC_OPEN

Formal NC issued/open.

🟠 AWAITING_DISPOSITION

Technical/contractual disposition pending.

🔵 DISPOSITION_APPROVED

Authorized disposition obtained.

🟡 CORRECTIVE_ACTION_IN_PROGRESS

Approved action being implemented.

🔵 READY_FOR_VERIFICATION

Correction complete and ready for verification/testing.

🟣 AWAITING_TECHNICAL_ACCEPTANCE

Physical correction verified, but required professional/specialist acceptance outstanding.

🟢 NC_CLOSED

All required disposition, correction, verification, testing and acceptance complete.

11. NC TRANSITION

NC_OPEN

↓

AWAITING_DISPOSITION

↓

DISPOSITION_APPROVED

↓

CORRECTIVE_ACTION_IN_PROGRESS

↓

READY_FOR_VERIFICATION

Then either:

No specialist sign-off needed

→ NC_CLOSED

or:

Specialist/professional acceptance needed

→ AWAITING_TECHNICAL_ACCEPTANCE

→ NC_CLOSED

If verification fails:

back to CORRECTIVE_ACTION_IN_PROGRESS

12. TEST STATUS

This is the area where the status model matters most.

Build 2 gives the complete failed-test chain:

Identify → control → document → notify → diagnose → correct → reinspect → retest → accept → close, retaining FAIL → CORRECTION → RETEST → PASS → ACCEPTANCE as one traceable chain.

Canonical states

⚪ NOT_SCHEDULED

Required test not yet planned.

🟡 PLANNED

Test identified/scheduled.

🔵 READY_TO_TEST

G-TST-01 passed.

🟠 TEST_IN_PROGRESS

Test underway.

🟢 PASSED

Required acceptance criterion met.

Important:

PASSED means test result, not necessarily final system acceptance.

🔴 FAILED

Test failed.

🟡 CORRECTION_REQUIRED

Failure documented and corrective action required/underway.

🔵 READY_FOR_RETEST

Correction and reinspection complete.

🟠 RETEST_IN_PROGRESS

Retest underway.

🟢 RETEST_PASSED

Retest passes.

🟣 AWAITING_SPECIALIST_ACCEPTANCE

Result exists but required authorized acceptance/sign-off remains pending.

⚫ TEST_CLOSED

Testing lifecycle fully complete and accepted.

13. TEST TRANSITION

Normal pass:

NOT_SCHEDULED

→ PLANNED

→ READY_TO_TEST

→ TEST_IN_PROGRESS

→ PASSED

→ AWAITING_SPECIALIST_ACCEPTANCE where required

→ TEST_CLOSED

Failure:

TEST_IN_PROGRESS

→ FAILED

→ CORRECTION_REQUIRED

→ READY_FOR_RETEST

→ RETEST_IN_PROGRESS

If fail again:

FAILED

and cycle continues with escalation.

If pass:

RETEST_PASSED

→ AWAITING_SPECIALIST_ACCEPTANCE where required

→ TEST_CLOSED

Build 2 explicitly says a repeated retest failure remains open and should trigger escalation/root-cause reassessment rather than endless blind repair cycles.

14. DON'T COLLAPSE PASSED AND ACCEPTED

This distinction is important enough to freeze.

A test may:

PASS technically

but still lack:

- witness signature;

- specialist acceptance;

- calibration evidence;

- complete report;

- required attachment.

Therefore:

PASSED ≠ TEST_CLOSED

Build 2 requires not just passing results but complete documentation, specialist acceptance and traceable records.

15. ACCEPTANCE / SYSTEM STATUS

This is the high-level status for a system, room, area, equipment package, or turnover package.

Build 2 already uses examples such as:

- Ready

- Accepted

- Pending

- Partial

- Open

across physical completion, testing, commissioning, records and acceptance.

I would normalize this to:

⚪ NOT_STARTED

System/area not sufficiently progressed.

🔵 CONSTRUCTION_IN_PROGRESS

Physical construction ongoing.

🟡 PHYSICALLY_COMPLETE

Physical installation complete enough, but testing/records/deficiencies may remain.

This is a very important state.

Physically complete ≠ quality complete.

🟠 TESTING_COMMISSIONING_PENDING

Physical completion achieved, but required testing/commissioning outstanding.

🟠 DOCUMENTATION_PENDING

Physical/testing may be complete, but required acceptance records are incomplete.

🔴 BLOCKED

Open deficiency, NC, failed test or missing acceptance blocks progression.

🔵 READY_FOR_ACCEPTANCE

All internal prerequisites satisfied; final required acceptance/release pending.

🟢 ACCEPTED

System/area formally acceptable for the relevant scope.

🟢 TURNOVER_READY

For closeout packages where all physical, testing, documentation and owner-readiness criteria align.

Build 2's electrical-room example explicitly says only when architectural, mechanical, electrical, fire/life-safety, access, testing, deficiencies, NCs and documentation all align is the room QUALITY COMPLETE / TURNOVER READY.

16. ACCEPTANCE SHOULD BE COMPOSITE

This is probably the most important architecture decision in Step 5.

Do not manually set:

“AHU-01 = Accepted”

without understanding its underlying dimensions.

Instead, system readiness can be derived from component statuses:

PHYSICAL

Complete?

QUALITY

Deficiencies/NCs closed?

TESTING

Tests passed/closed?

COMMISSIONING

Complete?

RECORDS

Complete?

SPECIALIST ACCEPTANCE

Complete?

Then overall status derives logically.

Build 2's acceptance review uses exactly those categories: physical completion, documentary completion, testing, deficiencies, specialist acceptance and turnover documentation.

17. COMPOSITE STATUS EXAMPLE

AHU-01

Physical: 🟢 Complete
Installation inspection: 🟢 Accepted
Mechanical testing: 🟢 Closed
Electrical acceptance: 🟢 Closed
Controls: 🟢 Complete
Start-up: 🟢 Passed
Functional test: 🟢 Passed
TAB: 🟢 Accepted
Deficiencies: 🟢 Closed
Records: 🟡 Partial

Overall:

🟠 DOCUMENTATION PENDING

not:

🟢 ACCEPTED

because Build 2 explicitly states that physical operation alone is not enough when required acceptance evidence is missing.

18. BLOCKING PRIORITY

When several child statuses exist, the overall status should follow the highest-severity blocker.

Suggested priority:

- 🔴 BLOCKED

- 🔴 failed/NC/open critical issue

- 🟣 awaiting technical acceptance

- 🟠 testing/commissioning/documentation pending

- 🟡 physical/inspection work in progress

- 🔵 ready for review/acceptance

- 🟢 accepted/closed

In other words:

one critical unresolved failure beats twenty green checkmarks.

19. CLOSED VS ACCEPTED

We should keep these conceptually distinct.

ACCEPTED

A work/system condition meets applicable quality requirements.

CLOSED

A record/process lifecycle has been fully resolved.

Examples:

Air Barrier
→ ACCEPTED

Deficiency DEF-017
→ CLOSED

Test TST-021
→ TEST_CLOSED

NC-004
→ NC_CLOSED

This avoids sloppy terminology.

20. COMPLETE VS ACCEPTED

Also distinct.

Complete

The work appears finished.

Accepted

The work was verified against requirements.

Build 2 repeatedly reinforces this.

For deficiencies:

correction being “done” does not equal verified closure.

For systems:

physical completion and documentary completion are both required for acceptance.

21. GLOBAL BLOCKER FLAGS

Separate from status, objects may carry flags:

- blocksConcealment

- blocksPour

- blocksBackfill

- blocksTesting

- blocksCommissioning

- blocksTurnover

- requiresSpecialist

- overdue

- highPriority

- reopened

- asBuiltImpact

Example:

status = CORRECTION_IN_PROGRESS

blocksTurnover = true

overdue = true

This is much better than inventing:

“Overdue Critical Turnover-Blocking Correction”

as a status. 😂

22. INVALIDATION / REOPEN RULE

Any previously accepted object can transition backward when affected by later work.

Examples:

Fire-rated wall

ACCEPTED

new conduit installed

→ ISSUE_OPEN or READY_FOR_REVIEW

until:

- penetration reviewed;

- firestop installed;

- evidence captured.

Build 2 explicitly says later modification to a controlled firestop penetration should cause it to be reopened/reinspected.

Roof

accepted membrane

new penetration

→ affected area re-review.

Test

passed

equipment materially modified afterward

→ previous acceptance may no longer cover modified condition.

So status needs:

previousStatus

and:

reopenedReason

conceptually, even if the MVP doesn't yet store project instances.

23. STATUS SHOULD BE SCOPE-BASED

Same rule as gates.

You shouldn't have:

Firestopping = Accepted

globally.

You have:

Firestop condition in the activity being considered = Accepted

or later, if project instances are ever built:

FS-024 = Closed

Same for:

- footing;

- wall;

- roof zone;

- service segment;

- equipment;

- test package.

The universal guide should teach this mental model even if it doesn't track live project data.

24. STATUS COLOR PHILOSOPHY

We don't need fancy colors yet, but the semantics should remain stable:

| Meaning | Visual Family |
| --- | --- |
| untouched / inactive | ⚪ neutral |
| informational / ready / awaiting review | 🔵 |
| warning / pending / incomplete | 🟡 / 🟠 |
| blocking / failed | 🔴 |
| specialist/external pending | 🟣 or 🔵 |
| accepted / closed | 🟢 |

We can decide exact visual styling in Build 5.

The important thing is never to use green for something merely “submitted” or “contractor says complete.”

25. GLOBAL STATE TRANSITION RULES

I would freeze these:

Rule 1

You cannot transition an issue directly:

OPEN → CLOSED

without verification.

Rule 2

You cannot transition a failed test:

FAILED → TEST_CLOSED

without correction/retest/authorized acceptance where required.

Rule 3

You cannot transition an activity:

ISSUE_OPEN → ACCEPTED

while its blocking issue remains open.

Rule 4

You cannot release a gate while a hard blocking prerequisite remains unresolved.

Rule 5

System acceptance cannot be green while required child processes are failed/open/pending.

Rule 6

Accepted status may be invalidated by later modification.

Rule 7

NOT_APPLICABLE requires contextual reason, not simply “I didn't inspect it.”

Rule 8

An external/specialist acceptance requirement should never be represented as QC inspector acceptance.

26. STATUS DERIVATION EXAMPLE — WALL CLOSURE

Suppose:

Framing: 🟢 Accepted
Insulation: 🟢 Accepted
Electrical rough-in: 🟢 Accepted
Mechanical rough-in: 🟢 Accepted
Firestop: 🔴 Issue Open
Access: 🟢 Accepted

Then:

G-INT-01 = 🔴 NOT READY

therefore:

Gypsum closure = BLOCKED

Even though 5 out of 6 inputs are green.

Exactly how a quality gate should behave.

27. STATUS DERIVATION EXAMPLE — FAILED PRESSURE TEST

Mechanical installation: 🟢 Accepted
Test readiness: 🟢 Ready
Pressure test: 🔴 Failed

System becomes:

🔴 BLOCKED / TEST FAILURE

Corrective action completed:

Test: 🔵 Ready for Retest

Retest passes:

Test: 🟢 Retest Passed

But specialist signature missing:

Test: 🟣 Awaiting Specialist Acceptance

Only after that:

Test: ⚫ Test Closed

Then downstream insulation/commissioning can proceed.

That mirrors Build 2's failed-test process accurately.

28. STATUS DERIVATION EXAMPLE — TURNOVER

Physical work: 🟢
Deficiencies: 🟢
NCs: 🟢
Testing: 🟢
Commissioning: 🟢
As-builts: 🟢
O&M: 🟢
Certificates: 🟡 incomplete
Warranties: 🟢

Then:

G-FINAL-01 = 🔴/🟡 NOT READY

depending on whether the missing certificate is a hard turnover requirement.

No amount of “but the room is finished” overrides that.

Build 2's final turnover checkpoint explicitly requires testing, documentation, owner readiness and formal acceptance, not merely physical completion.

29. IMPLEMENTATION MODEL

Codex should eventually receive separate enums rather than one enormous one.

Conceptually:

ActivityStatus

GateStatus

DeficiencyStatus

NCStatus

TestStatus

AcceptanceStatus

Then generic fields such as:

status

flags[]

blocking

reopened

The important point is:

different object types get the smallest status set appropriate to their lifecycle.

30. STEP 5 — FROZEN

We now have:

Activity status model ✓

Gate status model ✓

Deficiency status model ✓

NC status model ✓

Test/retest status model ✓

System/acceptance status model ✓

Complete vs Accepted distinction ✓

Accepted vs Closed distinction ✓

Passed vs Test Closed distinction ✓

Overdue as flag, not status ✓

Blocker flags ✓

Backward/invalidation transitions ✓

Composite status derivation ✓

Scope-based statuses ✓

Specialist acceptance boundary ✓

Illegal transition rules ✓

This is enough for the application architecture.

And one important conclusion emerges:

The MVP should probably not try to behave like live project-management software by storing all these statuses against actual work instances.

For the universal-guide MVP, this model primarily powers workflow diagrams, gate logic, Quick/Full/Learn guidance, and “what happens next?” navigation. We can leave actual persistent project status tracking for much later, if we ever want it.

That keeps the universal guide exactly within the boundary we established earlier: a sophisticated QC thinking and field-reference system, not a parallel CRT QMS.

Step 6 is the Invalidation Logic Registry — formally defining what kinds of later work should send a previously accepted condition back for review, and exactly which related nodes/gates are affected.

Yes. Step 6 is the Invalidation Logic Registry.

This is where we formally answer:

What kinds of later work can make a previously accepted condition no longer trustworthy, and what has to be rechecked because of it?

This matters because construction is dynamic. A wall, membrane, penetration, piece of equipment or test can be acceptable at 10:00 and then be materially changed at 14:00.

Build 2 already gives us the principle explicitly in several places. Firestop records must be reopened/reinspected if a controlled penetration is modified later. Corrective work must restore the full affected assembly and can itself create a new deficiency. A previously failed test cannot simply disappear after repair; correction, retest, acceptance and traceability must remain linked.

BUILD 3 — STEP 6

CANONICAL INVALIDATION LOGIC REGISTRY

1. Core rule

Acceptance applies to the condition that was actually inspected. If that condition is materially changed afterward, the affected acceptance must be reconsidered.

Not every tiny downstream activity should reopen everything.

Invalidation happens only when later work could reasonably affect:

- compliance;

- performance;

- continuity;

- geometry;

- accessibility;

- structural condition;

- fire/life-safety performance;

- test validity;

- evidence;

- record accuracy.

2. We need a separate invalidation registry

Do not store invalidation as ordinary INTERFACES_WITH relationships.

It has different logic.

Canonical object:

InvalidationRule {

trigger

affectedNode

affectedGate

severity

response

condition

}

For example:

trigger:

new penetration through accepted fire-rated wall

affectedNode:

10.1 Fire-Rated Walls

10.3 Firestopping

affectedGate:

G-INT-01

severity:

hard

response:

REOPEN_FOR_REVIEW

3. Canonical invalidation actions

We only need five.

| Action | Meaning |
| --- | --- |
| FLAG_FOR_REVIEW | Something changed; inspector should confirm impact |
| REOPEN_ACTIVITY | Previously accepted activity becomes reviewable again |
| REOPEN_GATE | Previously released gate must be reassessed |
| INVALIDATE_TEST | Previous test may no longer prove current condition |
| UPDATE_RECORD_REQUIRED | As-built/evidence/documentation must be revised |

These can occur together.

Example:

Equipment relocated:

REOPEN_ACTIVITY

- REOPEN_GATE

- INVALIDATE_TEST

- UPDATE_RECORD_REQUIRED

depending on what changed.

4. Invalidation severity

Three levels.

LOW

Change likely only affects documentation or local visual acceptance.

Response:
FLAG_FOR_REVIEW

MEDIUM

Change affects previously inspected work or interface.

Response:
REOPEN_ACTIVITY

HIGH

Change affects concealed work, safety, performance, testing or a gate.

Response:
REOPEN_ACTIVITY + REOPEN_GATE

and possibly:

INVALIDATE_TEST

5. CONCRETE / STRUCTURAL INVALIDATION

Trigger — reinforcement moved after inspection

Affected:

- 2.2 Foundation Reinforcement

- 2.4 Pre-Pour Quality Gate

- G-STR-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Severity:

HIGH

Trigger — embed / anchor / sleeve / conduit moved after pre-pour

Affected:

- 2.3 Embedded Items

- 11.8 Embedded Items

- applicable 9.1 / 9.6 / mechanical embed

- 2.4 Pre-Pour Quality Gate

- G-STR-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Potentially:

UPDATE_RECORD_REQUIRED

Severity:

HIGH

Build 2 specifically treats embeds, conduits, anchors, sleeves and openings as prerequisite items that must be verified before pour release.

Trigger — formwork altered after inspection

Affected:

- 2.1 Foundation Formwork

- 2.4

- G-STR-01

Severity:

HIGH

Trigger — supporting concrete modified after steel erection acceptance

Examples:

- anchor altered;

- concrete chipped;

- base modified.

Affected:

- 2.6 Foundation Concrete Acceptance

- 3.3 Structural Steel Erection

- connection/activity depending on support

Action:

FLAG_FOR_REVIEW
or
REOPEN_ACTIVITY

depending on significance.

6. BELOW-GRADE / BACKFILL INVALIDATION

Trigger — waterproofing damaged during backfill

Affected:

- 2.9 Below-Grade Waterproofing

- G-EXT-01 / relevant local pre-backfill release

- 1.6 or 2.12 backfill progression

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Severity:

HIGH

Build 2 gives this exact scenario: torn waterproofing during backfill requires local control, documentation, approved repair, reinspection and release before backfill resumes.

Trigger — buried service disturbed before covering

Affected:

- 12.1 Underground Services

- relevant mechanical/electrical activity

- G-EXT-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Potentially:

INVALIDATE_TEST

if the disturbance could affect a previously tested joint/system.

Severity:

HIGH

Trigger — service route/elevation changed

Affected:

- 12.1 Underground Services

- survey/layout

- relevant 8.x / 9.x

- 14.10 Redlines / As-Builts

Action:

REOPEN_ACTIVITY
UPDATE_RECORD_REQUIRED

Severity:

MEDIUM/HIGH

7. BUILDING ENVELOPE INVALIDATION

Trigger — later penetration through accepted envelope

Affected:

- 4.2 Air Barrier

- 4.3 Vapour Barrier where applicable

- 4.4 Thermal Insulation

- 5.x if roof

- 8.9 or 9.9 penetration activity

- 11.7 Universal Penetrations

- G-ENV-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Potentially:

INVALIDATE_TEST

if envelope testing already occurred and the new penetration affects the tested area.

Severity:

HIGH

Trigger — membrane damaged by later trade

Affected:

- 4.2 Air Barrier

- 5.4 Roofing Membrane if roof

- related flashing/sealant/interface

- applicable envelope gate

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Severity:

HIGH

Trigger — window / exterior door removed or reset

Affected:

- 4.8 Windows / Glazing
or

- 4.9 Exterior Doors

plus:

- 4.2 Air Barrier

- 4.4 Insulation

- 4.10 Sealants

- relevant flashing

- G-ENV-01

Potentially:

- 13.5 Building Envelope Testing

Action:

REOPEN_ACTIVITY
REOPEN_GATE
possibly INVALIDATE_TEST

Severity:

HIGH

Trigger — exterior sealant removed/reworked

Affected:

- 4.10 Sealants

- associated opening/interface

Action:

REOPEN_ACTIVITY

Testing only invalidated where the sealant is part of previously accepted/tested performance.

8. ROOF INVALIDATION

Roofing gets particularly strong invalidation logic because Build 2 explicitly stages acceptance before later equipment/traffic obscures the membrane.

Trigger — new roof penetration

Affected:

- 5.4 Roofing Membrane

- 5.5 Flashings

- 5.6 Roof Penetrations

- 5.3 insulation locally

- 5.2 air/vapour layer locally

- 11.7 Universal Penetrations

- related 8.9 / 9.9

- G-ROOF-01D

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Potential:

INVALIDATE_TEST

Severity:

HIGH

Trigger — membrane punctured/damaged by traffic

Affected:

- 5.4 Roofing Membrane

- 5.9 Roofing Final Inspection

- G-ROOF-01D/E as applicable

Action:

REOPEN_ACTIVITY
possibly REOPEN_GATE

Severity:

HIGH

Trigger — rooftop equipment/curb modified

Affected:

- 5.7 Curbs & Equipment Interfaces

- 5.4 membrane

- 5.5 flashing

- 5.6 penetrations

- 8.6/9.4 equipment

- 11.9 equipment base/interface

- 11.10 access

Potential:

UPDATE_RECORD_REQUIRED

Severity:

HIGH

Trigger — roof drain altered

Affected:

- 5.8 Roof Drains

- 8.3 Storm Drainage

- roof slope/drainage acceptance

- 5.9 Final Inspection

Potential:

INVALIDATE_TEST

if drainage testing already completed.

9. INTERIOR / ARCHITECTURAL INVALIDATION

Trigger — new rough-in after wall pre-concealment acceptance

Affected:

- applicable 8.x or 9.x

- 6.2 Framing if altered

- 6.3 Insulation

- 6.5 Fire-Rated Assemblies if rated

- 10.3 Firestopping if penetrated

- G-MEP-01

- G-INT-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Severity:

HIGH

Trigger — wall/ceiling reopened after closure

Affected:

- 6.4 Gypsum Board or 6.8 Ceilings

- concealed work in affected area

- fire/acoustic condition

- insulation

- relevant MEP

Action:

FLAG_FOR_REVIEW

Escalate to:

REOPEN_ACTIVITY

for anything physically disturbed.

Severity:

MEDIUM/HIGH

Trigger — access panel removed/relocated

Affected:

- 6.9 Access Panels

- 11.10 Access & Maintainability

- related valve/damper/control/equipment

Action:

REOPEN_ACTIVITY

Potentially:

REOPEN_GATE

if closure would leave required component inaccessible.

10. FIRE / LIFE-SAFETY INVALIDATION

This should be among the strongest logic in the entire registry.

Trigger — new penetration through accepted rated wall/floor

Affected:

- 10.1 Fire-Rated Wall
or

- 10.2 Fire-Rated Floor/Ceiling

- 10.3 Firestopping

- 6.5 Fire-Rated Assemblies

- 11.7 Universal Penetrations

- G-INT-01

- potentially G-LS-01

Action:

REOPEN_ACTIVITY
REOPEN_GATE

Severity:

HIGH

Build 2 explicitly says the penetration must be reopened/reinspected if modified later.

Trigger — existing firestop damaged/removed

Affected:

- 10.3 Firestopping

- parent rated assembly

- life-safety readiness where relevant

Action:

REOPEN_ACTIVITY
potential REOPEN_GATE

Severity:

HIGH

Trigger — fire/smoke damper relocated or disturbed

Affected:

- 10.4 Damper

- 8.5 HVAC Ductwork

- 6.9 Access

- 8.8 BAS

- 10.6 Fire Alarm interface

- G-LS-01

Potential:

INVALIDATE_TEST

if functional/integrated testing already occurred.

Severity:

HIGH

Trigger — fire-rated door hardware modified

Affected:

- 6.7 Door Hardware

- 10.5 Fire-Rated Doors

- potentially 10.7 Life-Safety Interfaces

Potential:

INVALIDATE_TEST

if operation/closing/latching test no longer represents current assembly.

11. MECHANICAL INVALIDATION

Trigger — piping repaired after passed pressure test

Affected:

- relevant 8.1 / 8.2 / 8.3 / 8.4

- 8.10 Mechanical Testing

- 13.3 Mechanical Testing

Action:

REOPEN_ACTIVITY
INVALIDATE_TEST

Severity:

HIGH

Because the tested configuration is no longer the current configuration.

Trigger — ductwork modified after leakage/TAB/functional acceptance

Affected:

- 8.5 HVAC Ductwork

- 8.10 Mechanical Testing

- TAB/functional test as applicable

- 13.3 / 13.6

Action:

REOPEN_ACTIVITY

Potential:

INVALIDATE_TEST

depending on modification.

Trigger — equipment relocated

Affected:

- 8.6 HVAC Equipment

- 11.9 Equipment Bases

- 11.10 Access

- piping/duct/drain interfaces

- 9.5 electrical distribution

- 8.8 controls

- 13.7 Start-Up

- 13.6 Functional Testing

- 14.10 As-Builts

Action:

REOPEN_ACTIVITY
UPDATE_RECORD_REQUIRED

Likely:

INVALIDATE_TEST

where startup/function was already completed.

Severity:

HIGH

12. ELECTRICAL INVALIDATION

Technical acceptance remains with authorized specialists, but our quality logic can still identify when previous evidence may no longer apply.

Trigger — raceway route modified after concealed-work inspection

Affected:

- 9.1 Conduits/Raceways

- penetration/support nodes as applicable

- G-MEP-01 / G-INT-01 if concealment involved

- 14.10 As-Builts

Action:

REOPEN_ACTIVITY
UPDATE_RECORD_REQUIRED

Trigger — tested cable/equipment altered after testing

Affected:

- applicable electrical installation

- 9.11 Electrical Testing Interfaces

- 13.4 Electrical Testing Interfaces

Action:

FLAG_FOR_REVIEW
potential INVALIDATE_TEST

Actual retest requirement comes from project procedure / authorized specialist.

Build 2 specifically requires the inspector to ensure the correct system is tested using current procedures and that failed/retested conditions remain traceable, without assuming technical acceptance authority.

Trigger — grounding/bonding connection changed after test

Affected:

- 9.6 Grounding/Bonding

- 9.11

- 13.4

Action:

REOPEN_ACTIVITY
potential INVALIDATE_TEST

Severity:

HIGH

13. TEST INVALIDATION

This needs a general rule.

A previously passed test may no longer represent the current condition if:

- tested component is replaced;

- system configuration changes;

- tested joint/connection is disturbed;

- control logic changes;

- test boundary changes;

- relevant repair is performed;

- equipment is relocated;

- supporting conditions materially change.

Response:

INVALIDATE_TEST

or, when applicability isn't certain:

FLAG_FOR_REVIEW_BY_AUTHORIZED_PERSON

That is important. The guide should not automatically prescribe technical retesting where project requirements determine it.

14. FAILED-TEST CORRECTION IS NOT AUTOMATIC VALIDATION

Build 2 is explicit:

Correction does not close the failed test. It must be reinspected, retested and accepted.

Therefore:

FAILED

→ correction

does not

→ PASSED

Instead:

FAILED
→ CORRECTION_REQUIRED
→ READY_FOR_RETEST
→ RETEST
→ PASS
→ acceptance
→ closed.

We already set this in Step 5; Step 6 reinforces it as an invalidation rule.

15. CORRECTIVE WORK CAN INVALIDATE ADJACENT WORK

Very important.

Build 2 explicitly says corrective work must restore adjacent systems, and the correction itself can be deficient.

Example:

Repairing damaged waterproofing may involve:

- removing insulation;

- disturbing protection board;

- exposing sealant;

- moving adjacent drainage.

Therefore:

Corrective-action rule

Whenever correction touches another accepted system:

FLAG_ADJACENT_ACCEPTED_WORK_FOR_REVIEW

This should apply universally.

16. DOCUMENT CHANGE INVALIDATION

Not all invalidation comes from physical work.

Trigger — revised approved drawing / technical change

Potentially affected:

- any activity based on superseded information;

- pending inspection;

- accepted but not yet covered work;

- as-built status.

Action depends on timing:

Work not yet started

→ update reference only.

Work in progress

→ FLAG_FOR_REVIEW.

Work already accepted

→ compare installed condition to revision.

If incompatible:

REOPEN_ACTIVITY

Test based on superseded configuration

→ FLAG_FOR_REVIEW
possibly INVALIDATE_TEST.

17. MATERIAL SUBSTITUTION INVALIDATION

Trigger — approved material/system changes

Affected:

- material-control acceptance;

- activity depending on that product;

- compatibility interfaces;

- testing where product affects performance.

Examples:

- sealant;

- membrane;

- firestop;

- insulation;

- coating;

- equipment.

Action:

REOPEN_ACTIVITY

Potentially:

- specialist review;

- new testing;

- new compatibility check.

18. TEMPORARY CONDITION INVALIDATION

Sometimes accepted work remains physically untouched but surrounding conditions change.

Examples:

- stored material damages roof membrane;

- water ingress wets accepted insulation;

- freeze/thaw damages unfinished concrete;

- protection removed;

- finished surface damaged by subsequent trade.

Response:

FLAG_FOR_REVIEW

If damage observed:

REOPEN_ACTIVITY.

19. ACCESS INVALIDATION

Any later work that blocks access to a previously acceptable maintainable component affects:

- 11.10 Access & Maintainability

- related equipment/system

- possibly commissioning/turnover readiness.

Examples:

- duct blocks valve;

- ceiling grid blocks access panel;

- cable tray blocks equipment removal;

- new pipe blocks panel clearance.

Action:

REOPEN_ACTIVITY
and potentially:

REOPEN_GATE

for commissioning/turnover.

20. AS-BUILT INVALIDATION

If final installed condition changes after redline/as-built status was considered complete:

Affected:

- 14.10 Redlines/As-Builts

- 14.14 Final Quality Records

- G-FINAL-01 if closeout already underway.

Action:

UPDATE_RECORD_REQUIRED

This should not necessarily reopen physical quality acceptance.

That's why document invalidation needs its own action.

21. TURNOVER INVALIDATION

Before formal turnover, discovery of any unresolved condition that affects required acceptance must be able to pull:

G-FINAL-01 = READY

back to:

IN_REVIEW or NOT_READY.

Triggers include:

- newly discovered deficiency;

- reopened NC;

- missing test;

- invalidated test;

- incomplete as-built;

- missing O&M/certificate/warranty;

- life-safety issue;

- previously accepted work modified.

Build 2 explicitly requires physical completion, closed deficiencies/NCRs, complete testing/commissioning, records, owner readiness and required acceptance before turnover.

22. INVALIDATION PROPAGATION RULES

This is where we prevent chaos.

When one node is invalidated, we do not recursively reopen the entire project.

We use controlled propagation.

Level 1 — Direct node

Always consider.

Example:

new roof penetration

→ 5.6 Roof Penetrations reopened.

Level 2 — Directly affected interfaces

Only where physically/functionally affected.

→ 5.4 membrane
→ 5.3 insulation
→ 5.2 control layer
→ electrical/mechanical penetration.

Level 3 — Gate

Reopen if the affected node was a prerequisite of that gate.

→ G-ROOF-01D.

Level 4 — Test

Invalidate only where change could affect test validity.

Level 5 — Higher acceptance

Downgrade system/turnover status only if unresolved invalidation is a required acceptance dependency.

No infinite cascade.

23. LOCAL SCOPE RULE

This is essential.

A defect in one roof penetration should not mark:

Entire Roofing = Failed

unless the nature of the condition genuinely affects the whole system.

Invalidation should apply to the smallest defensible scope:

- component;

- penetration;

- wall;

- room;

- roof zone;

- system segment;

- equipment;

- test package.

Then broaden only where evidence justifies it.

24. INVALIDATION DOES NOT EQUAL FAILURE

Important distinction.

A change can mean:

FLAG_FOR_REVIEW

without meaning:

NON-CONFORMING

Example:

Approved equipment was relocated according to a new approved drawing.

The old inspection is no longer sufficient.

But that does not mean the new installation is wrong.

So:

Invalidated = prior evidence may no longer prove the current condition.

Not:

Invalidated = defect.

25. REOPEN REASON CATEGORIES

To keep the future UI simple, use a short canonical list:

| Code | Reason |
| --- | --- |
| PHYSICAL_MODIFICATION | Accepted work physically changed |
| NEW_PENETRATION | New opening/service through accepted assembly |
| DAMAGE | Accepted work damaged |
| REPAIR | Repair affects accepted condition |
| DESIGN_CHANGE | Approved technical/design change |
| MATERIAL_CHANGE | Product/material changed |
| CONFIGURATION_CHANGE | System/equipment arrangement changed |
| FAILED_TEST | Test failure affects acceptance |
| TESTED_CONDITION_CHANGED | Previously tested configuration altered |
| ACCESS_CHANGE | Maintainability/access affected |
| DOCUMENT_CHANGE | Record/as-built/reference no longer current |
| LATER_TRADE_IMPACT | Subsequent trade affects accepted work |

That's enough.

26. INVALIDATION RESPONSE MATRIX

| Trigger | Activity | Gate | Test | As-Built |
| --- | --- | --- | --- | --- |
| Physical modification | Reopen | If prerequisite | If test affected | Maybe |
| New penetration | Reopen | Usually | Maybe | Usually |
| Damage | Reopen | Maybe | Maybe | No |
| Repair | Reinspect | Maybe | Maybe | Maybe |
| Design change | Review | Maybe | Maybe | Usually |
| Material change | Review/Reopen | Maybe | Maybe | Maybe |
| Equipment relocation | Reopen | Commissioning gate | Usually review | Yes |
| Failed test | Issue state | Downstream blocked | Failed | No |
| Access blocked | Reopen access | Maybe | Functional maybe | Maybe |
| Record/configuration mismatch | Physical review | Final gate maybe | No unless affected | Yes |

27. USER-FACING LANGUAGE

Do not expose “INVALIDATION ENGINE” everywhere in the field interface.

The user should see something simple like:

⚠ Previously Accepted Work May Be Affected

Why?

New penetration added after inspection.

Recheck

- Fire-rated assembly

- Firestop

- MEP penetration

- Wall closure readiness

or:

⚠ Previous Test May No Longer Represent Current Condition

Equipment configuration changed after testing.

Next

Verify retest requirements with applicable project procedure / authorized specialist.

Much better than developer terminology.

28. QC THINK CONNECTION

This should eventually feed Build 5's QC THINK function.

One of its questions should be:

Has anything changed since this work was last inspected or tested?

That single question catches:

- new penetrations;

- repairs;

- relocated services;

- damage;

- technical changes;

- changed test conditions.

Very valuable.

29. INVALIDATION + EVIDENCE

Whenever accepted work is reopened, the previous evidence should remain.

Never overwrite:

Before Modification — Accepted

with:

After Modification — Accepted

The history should conceptually remain:

Initial condition
→ accepted

Modification
→ acceptance reopened

Reinspection
→ accepted again

This mirrors Build 2's approach to failed tests, where the original failure remains part of the final traceable chain rather than being replaced by the passing result.

30. STEP 6 — FROZEN

We now freeze:

Invalidation actions ✓

Low / Medium / High invalidation severity ✓

Structural/pre-pour invalidation ✓

Below-grade/backfill invalidation ✓

Envelope invalidation ✓

Roofing invalidation ✓

Interior/pre-concealment invalidation ✓

Fire/life-safety invalidation ✓

Mechanical invalidation ✓

Electrical/specialist-interface invalidation ✓

Test invalidation ✓

Corrective-work impact on adjacent work ✓

Design/document/material-change invalidation ✓

Access invalidation ✓

As-built invalidation ✓

Final turnover invalidation ✓

Controlled propagation ✓

Smallest-defensible-scope rule ✓

Invalidation ≠ non-conformance ✓

Reopen-reason registry ✓

Historical evidence preservation ✓

The architecture is now getting very robust:

Build 2 tells us what good QC looks like.

Build 3 now knows what connects to what, what must happen first, what gates progression, what statuses mean, and what later events can reopen previously accepted work.

Step 7 is the Common Activity-Page Schema. That is where we finally define the exact information structure that every activity page—Concrete, Air Barrier, Ductwork, Firestop, Electrical Equipment, Testing, etc.—will inherit before Build 5 turns it into Quick / Full / Learn presentation.

Yes. Step 7 is the Common Activity-Page Schema.

This is the point where we stop talking about the graph abstractly and define the exact information structure every technical activity page inherits.

The goal is consistency:

Whether you open 2.2 Foundation Reinforcement, 4.2 Air Barrier, 8.9 Mechanical Penetrations, 9.4 Electrical Equipment, or 10.3 Firestopping, your brain should know where every type of information lives.

Build 2 already gives us the repeated backbone: Requirements → Planning → Document Control → Material Control → Inspection/Test → Records → NC/Deficiency → Corrective Action → Verification → Closure → Reporting/Analysis → Quality Checkpoint. That structure appears even in very different modules such as embedded items, finishes, controls, penetrations, closeout records and technical documentation.

BUILD 3 — STEP 7

CANONICAL ACTIVITY-PAGE SCHEMA

I would split every page into four layers:

IDENTITY → FIELD NAVIGATION → BUILD 2 TECHNICAL CONTENT → CONTROL / REFERENCE

That separation will make Build 5 much easier because Quick / Full / Learn can expose different parts of the same underlying object instead of us creating three separate pages.

1. ACTIVITY IDENTITY

Every page starts with a small immutable identity block.

Required fields

| Field | Meaning |
| --- | --- |
| id | Canonical Build 2 ID |
| sectionId | Parent section |
| title.en | Canonical English title |
| title.fr | Added in Build 4 |
| nodeTags[] | activity/interface/gate/etc. |
| qualityObjective | Build 2 objective |
| applicability | When this activity applies |
| authorityNote | Specialist boundary where relevant |

Example:

8.9 Mechanical Penetrations

Quality objective

Ensure every mechanical penetration is correctly located and sized, structurally coordinated, properly sleeved/sealed, and restores required fire, air, water, acoustic and finish performance. Build 2 expressly treats the penetration as simultaneously mechanical, structural, architectural/envelope and fire/life-safety work.

2. FIELD NAVIGATION BLOCK

This is Build 3 information, not Build 2 technical content.

Every normal activity page can contain:

BEFORE

Derived from REQUIRES.

GATES

Derived from GATED_BY.

INTERFACES

Derived from INTERFACES_WITH.

UNIVERSAL WORKFLOWS

Examples:

- Universal Penetrations

- Access & Maintainability

TESTING

Derived from TESTED_BY.

COMMISSIONING

Derived from COMMISSIONED_BY.

AFTER

Reverse dependency lookup.

CLOSEOUT

Relevant closeout/as-built links.

These are all generated from our relationship model. They should not be manually rewritten into every activity.

3. QUALITY OBJECTIVE

This stays directly from Build 2.

Every activity should answer:

What does successful quality control of this activity actually achieve?

This matters because a checklist without an objective encourages mechanical box-ticking.

Examples from Build 2 include roof drains being controlled not simply for installation but so water reaches the drainage system without ponding or leakage, and acceptance evidence demonstrating that systems are inspected, tested, corrected where necessary, properly accepted and turnover-ready.

4. REQUIREMENTS — WHERE TO GET THEM

Canonical field:

requirements[]

This keeps the Build 2 concept exactly.

Possible categories:

Drawings

- architectural;

- structural;

- mechanical;

- electrical;

- civil;

- life-safety.

Specifications

Approved Shop Drawings / Submittals

PIE / PRIE

Procedures

Manufacturer Information

Technical Changes

- directives;

- approved RFI/QMT responses;

- revised details.

Standards / acceptance requirements where identified by governing project documents

The activity page should not invent actual project criteria.

It tells you where to look.

For example, Build 2's mechanical penetration module pulls from mechanical drawings, structural opening drawings, architectural details, firestop systems, waterproofing and air-barrier details, roof details, sleeve details, coordination drawings and PIE/PRIE.

5. PLANNING

Canonical field:

planning[]

This answers:

What should I establish before walking into the inspection?

Typical categories:

Scope

What work/area/system am I inspecting?

Sequence

What comes before/after?

Inspection timing

Before installation?
During?
Before concealment?
After completion?

Hold / witness / review considerations

Interfaces

Which other disciplines must be coordinated?

Access

Testing preparation

Evidence plan

What conditions may disappear before I can return?

Build 2 repeatedly uses this planning stage to stop QC becoming reactive. For embeds, for example, it calls for a multidisciplinary embed walkdown before the pour; for equipment bases, it requires the final equipment model, footprint, anchor pattern, stub-ups, orientation, access and vibration requirements to be reviewed before pad placement.

6. DOCUMENT CONTROL

Canonical field:

documentControl[]

This is one of our most important universal patterns.

Every activity should ask:

Are the documents current?

Do drawing/detail/shop-drawing references agree?

Is the correct revision being used?

Are approved technical changes incorporated?

Are superseded documents excluded?

Are IDs consistent?

Are required signatures/approvals present?

This should be short but always present.

Build 2's final records logic specifically emphasizes correct revisions, signatures, equipment/system IDs, indexing and removal/identification of superseded records.

7. MATERIAL / EQUIPMENT CONTROL

Canonical field:

materialControl[]

The title should adapt slightly by activity:

Material Control

or

Material / Equipment Control

Typical checks:

- approved product;

- correct type/grade/model;

- identification;

- quantity;

- certifications;

- damage;

- storage;

- shelf life;

- compatibility;

- accessories;

- manufacturer requirements.

For documentation-heavy closeout nodes, this can become a comparison of physical equipment against records rather than literal material receiving. Build 2 does exactly that for O&M documentation and warranties.

8. INSPECTION / TESTING

This is the main technical execution block.

Canonical structure:

inspection {

before[]

during[]

after[]

testing[]

}

Not every activity needs all four.

For example:

Concrete

Before

- formwork;

- reinforcement;

- embeds.

During

- placement;

- consolidation;

- sampling.

After

- curing;

- surface;

- geometry.

Roof Drain

The Build 2 inspection checks location, elevation, connection, membrane integration, surrounding slope and overflow, followed by drainage verification.

Mechanical Penetration

Check location, opening size, sleeve, clearance, structural damage, configuration, firestop, air/water seal, insulation continuity and finish closure.

So this field has to support subgroups, not one huge checklist.

9. SPECIALIST BOUNDARY

This should exist only when applicable.

Canonical fields:

specialistBoundary {

required: true/false

inspectorRole

specialistRole

escalationNote

}

Example for emergency lighting:

Inspector verifies physical location, orientation, visibility and mounting.

Required functional testing is performed/accepted by authorized electrical personnel.

Build 2 explicitly makes that distinction.

This protects against false autonomy.

10. RECORDS / OBJECTIVE EVIDENCE

Canonical field:

evidence[]

This should answer:

If someone challenges this inspection six months later, what proves what I saw and what happened?

Possible evidence categories:

Identification

- activity;

- location;

- system/equipment ID.

Documents

- drawing/detail reference;

- submittal;

- procedure.

Measurements

- dimensions;

- elevations;

- test readings;

- thickness.

Photos

- overall;

- detail;

- pre-concealment;

- before/after.

Test records

Signatures/witnesses

Certificates

Correction evidence

Build 2 is very consistent about this. Mechanical penetrations, for example, retain penetration ID/location, wall/floor type, service, firestop system, before/after photos and approval reference. Final acceptance evidence expands this to inspection forms, test reports, commissioning/start-up records, specialist reports, photos, deficiency/NC closure, as-builts, O&M, warranties and acceptance forms.

11. NC / DEFICIENCY

Canonical field:

issues {

commonDeficiencies[]

escalationTriggers[]

}

This does not contain a whole separate deficiency workflow.

It answers:

What commonly goes wrong here?

Example mechanical penetration:

- unauthorized core hole;

- oversized opening;

- cut reinforcement;

- missing sleeve;

- missing firestop;

- poor roof flashing;

- unsealed air-barrier interface;

- damaged insulation.

If an issue is actually found, navigation sends you to the common Section 14 lifecycle we already built.

12. CORRECTIVE ACTION

Canonical field:

correctiveAction[]

This should not provide unsupported engineering repair instructions.

It should define the quality-control workflow:

identify → control → document → communicate → obtain/confirm authorized correction → execute → inspect → retest if required → document.

For simple work, Build 2 may contain a straightforward accepted repair approach.

For technically sensitive work:

obtain authorized disposition.

Build 2's mechanical penetration example does exactly this when an opening falls outside an approved firestop system range: document dimensions, control closure, obtain a suitable listed system or authorized disposition, install, inspect, label/document, close.

13. VERIFICATION

Canonical field:

verification[]

This answers:

How do I prove the correction or installation is actually acceptable?

Typical checks:

- physical correction;

- restored adjacent systems;

- measurement;

- function;

- test/retest;

- specialist acceptance;

- documentation;

- no secondary damage.

This stays separate from corrective action because:

repair performed ≠ repair verified.

Build 2's corrective-work module explicitly requires checking the full affected assembly, not merely the repaired piece.

14. CLOSURE

Canonical field:

closureCriteria[]

This is a checklist defining:

What must be true before this activity can legitimately be considered accepted/complete?

This should be one of the strongest fields in the whole application.

Example controls/BAS closure from Build 2:

- devices installed;

- tags correct;

- access adequate;

- equipment association correct;

- functional test passed;

- commissioning record complete.

Example roof drain:

- correct drain;

- correct elevation;

- complete connection;

- membrane integrated;

- sump correct;

- drainage functional;

- test complete.

15. REPORTING / ANALYSIS

Canonical field:

reportingAnalysis[]

This should be relatively small.

Purpose:

What should recurring observations from this activity tell quality management?

Examples:

- repeat workmanship problem;

- repeated failed test;

- coordination issue;

- supplier/material issue;

- trade issue;

- design/constructability issue;

- systemic process breakdown.

Build 2 frequently uses this field for trends, such as repeated controls/commissioning failures, recurring fixture/ceiling coordination issues, and repeated document gaps.

This is the field that gradually teaches managerial-quality thinking.

16. QUALITY CHECKPOINT

Canonical field:

qualityCheckpoint[]

This is not another inspection checklist.

It is the final compact:

Did I cover the important quality controls for this activity?

This should eventually power Quick Mode heavily.

For example, Build 2's embedded-item checkpoint condenses the whole activity to structural, mechanical, electrical, architectural, equipment, location, elevation, orientation, secure fixing and pre-pour evidence.

The roof-drain checkpoint similarly collapses the module to drain ID, location, elevation, connection, sump/taper, membrane clamp, strainer, overflow and drainage test.

That is exactly why this field should remain distinct.

17. WATCH FOR

This is Build 5 content, but we should reserve the data field now.

Canonical:

watchFor[]

It will contain the highest-value visual/field risks extracted from:

- common deficiencies;

- inspection points;

- failure examples.

Example Air Barrier:

tears
incomplete transitions
poorly sealed penetrations
damage from later trades.

We populate/polish this during Build 5.

18. DON'T MISS

Also reserve now:

dontMiss[]

This is even shorter than Watch For.

Maximum ideally:

1–3 critical reminders.

Examples:

Firestop

Confirm the installed condition matches an approved system before concealment.

Concrete

Verify every embed and MEP cast-in before pour release.

Roof

Inspect penetrations and membrane before later equipment/traffic obscures them.

Build 5 will determine exact wording.

19. WHY IT MATTERS

Reserve:

whyItMatters

This supports Learn Mode.

Short technical reasoning.

Not another textbook.

Example:

Incomplete air-barrier continuity at penetrations can compromise the performance of the entire enclosure even when large membrane areas appear acceptable.

This will mostly be synthesized from Build 2 objectives and examples.

20. PRACTICAL EXAMPLE

Canonical:

examples[]

Build 2 already contains excellent scenarios.

Examples include:

- torn waterproofing during backfill;

- oversized rated-wall penetration;

- ponding away from roof drain;

- coating thickness below requirement;

- equipment/controls commissioning failures.

These should be retained because they turn abstract controls into field reasoning.

21. PRE-CONCEALMENT FIELD

Canonical:

preConcealment {

applies

criticalChecks[]

evidence[]

relatedGateId

}

Only used where relevant.

Examples:

- reinforcement;

- embeds;

- underground services;

- envelope membranes;

- firestop;

- MEP rough-in;

- roof layers.

This is what eventually powers:

BEFORE CLOSING / BEFORE COVERING

without duplicating a new checklist.

22. STATUS / LOGIC METADATA

Even though the universal-guide MVP isn't a project tracker, reserve:

logic {

statusFamily

applicableGates[]

invalidationRules[]

}

So the page knows:

- which status model applies;

- which gates control it;

- what could invalidate acceptance.

This is behind-the-scenes data.

It doesn't need to clutter the field page.

23. SEARCH / TERMINOLOGY METADATA

Reserve for Build 4 and Build 6:

search {

aliases.en[]

aliases.fr[]

acronyms[]

keywords[]

}

Example:

2.2 Foundation Reinforcement

could eventually understand:

- reinforcement;

- rebar;

- reinforcing steel;

- armature;

- acier d'armature.

Same page. No duplicate content.

24. COMPLETE CANONICAL ACTIVITY OBJECT

Conceptually, Codex should eventually be able to represent any normal activity as:

Activity {

id

sectionId

title {

en

fr

}

nodeTags[]

qualityObjective

applicability

authorityNote

requirements[]

planning[]

documentControl[]

materialControl[]

inspection {

before[]

during[]

after[]

testing[]

}

specialistBoundary

evidence[]

issues {

commonDeficiencies[]

escalationTriggers[]

}

correctiveAction[]

verification[]

closureCriteria[]

reportingAnalysis[]

qualityCheckpoint[]

watchFor[]

dontMiss[]

whyItMatters

examples[]

preConcealment {

applies

criticalChecks[]

evidence[]

relatedGateId

}

search {

aliasesEn[]

aliasesFr[]

acronyms[]

keywords[]

}

logic {

statusFamily

gateIds[]

invalidationRuleIds[]

}

}

And separately:

relationships do not live manually inside the page.

The graph registry supplies them.

That's crucial.

25. NAVIGATION DATA SHOULD REMAIN SEPARATE

We should not embed:

before[]

after[]

interfaces[]

testingLinks[]

inside each activity object manually.

Why?

Because Step 2 already owns those relationships.

Instead:

Activity page loads 8.9

↓

relationship engine asks:

What does 8.9 REQUIRE?
What INTERFACES_WITH 8.9?
What TESTS 8.9?
What GATES control 8.9?

↓

UI renders it.

One source of truth.

No duplication.

26. NOT EVERY NODE USES THE NORMAL ACTIVITY TEMPLATE

Important.

The schema above is the base schema, but four specialized page types should inherit/adapt it:

Gate pages

Use:

- purpose;

- inputs;

- checks;

- blockers;

- release;

- invalidation.

Testing pages

Emphasize:

- readiness;

- procedure;

- instruments;

- test execution;

- result;

- fail/retest;

- acceptance evidence.

Interface pages

Emphasize:

- systems involved;

- sequence;

- compatibility;

- cross-discipline checks;

- final interface condition.

Closeout pages

Emphasize:

- records;

- status;

- assignment;

- correction;

- verification;

- acceptance.

But they should still feel visually related.

We do not want four completely unrelated UI designs.

27. PAGE INFORMATION PRIORITY

Even though we're not doing Build 5 yet, Step 7 needs to establish priority.

Tier 1 — Field-critical

- objective;

- checkpoint;

- before/gate;

- inspection;

- interfaces;

- evidence;

- watch-for;

- closure.

Tier 2 — Preparation/reference

- requirements;

- planning;

- document control;

- material control;

- specialist boundary.

Tier 3 — Deep/reference

- corrective-action examples;

- reporting/analysis;

- why it matters;

- detailed examples.

This becomes the foundation for:

QUICK / FULL / LEARN

later.

28. COMMUNICATIONS

There is one thing from your original concept that we should explicitly preserve, because Build 2 often embeds notification/coordination inside planning, failed-test control and corrective actions rather than always giving it its own numbered subsection.

We should add:

communications {

before[]

during[]

issueEscalation[]

after[]

}

This answers:

Before

Who must know the inspection/test is coming?

During

Who needs to be present/witness?

Issue

Who gets informed when something is wrong?

After

What needs to be transmitted/reported?

This is important enough that I would make it a canonical field even though Build 2 doesn't always give it its own .13 heading.

Build 2's failed-test process, for example, explicitly requires notifying the responsible trade, Responsable qualité and specialist as part of the controlled failure workflow.

This preserves your original Inputs → Process → Outputs → Communications concept.

29. OUTPUTS

Likewise, let's explicitly classify the end products.

Canonical:

outputs {

records[]

acceptanceEvidence[]

followUp[]

}

This doesn't duplicate evidence[].

It answers:

At the end of this activity, what should exist?

For example:

Reinforcement pre-pour

- completed inspection;

- photographs;

- dimensions;

- released gate;

- deficiency record if applicable.

Mechanical test

- test report;

- pass/fail;

- correction/retest chain if failed;

- specialist acceptance.

O&M closeout

- accepted final manual/package.

Build 2's acceptance-evidence section is particularly explicit that the final output should reconstruct the full system story from inspection through test, correction, retest and acceptance.

30. FINAL PAGE SCHEMA — FROZEN

So the canonical normal activity page now consists of:

IDENTITY

ID
Title
Quality Objective
Applicability
Authority Boundary

NAVIGATION

Before
Gate
Interfaces
Universal Workflows
Testing
Commissioning
After
Closeout

TECHNICAL CONTROL

Requirements
Planning
Document Control
Material / Equipment Control
Inspection / Testing
Records / Evidence
NC / Deficiency
Corrective Action
Verification
Closure
Reporting / Analysis
Quality Checkpoint

FIELD INTELLIGENCE

Watch For
Don't Miss
Why It Matters
Practical Examples
Pre-Concealment

MANAGEMENT / TRACEABILITY

Communications
Outputs
Status Family
Gate Associations
Invalidation Logic
Search / Terminology Metadata

That is the entire page model.

And most importantly:

We are not adding new technical work. We are organizing everything we already built into predictable information slots.

That means when we eventually process Build 2 into application data, every paragraph has somewhere obvious to go.

STEP 7 — FROZEN

Common activity object ✓

Build 2 twelve-stage technical structure preserved ✓

Navigation separated from technical content ✓

Evidence separated from outputs ✓

Communications restored as explicit canonical field ✓

Pre-concealment metadata ✓

Specialist/authority boundary ✓

Watch For / Don't Miss reserved for Build 5 ✓

Search/translation metadata reserved for Build 4/6 ✓

Gate/invalidation metadata linked, not duplicated ✓

Specialized page families identified ✓

Information priority tiers established ✓

That leaves Step 8 — Cross-Link Matrix Normalization / Final Build 3 Consolidation.

That should be the final Build 3 step: we take Steps 1–7 and define one clean master data model showing exactly how Sections, Activities, Relationships, Gates, Status Families and Invalidation Rules connect, resolve any remaining duplication, and then declare Build 3 architecturally frozen before moving to Build 5.

Yes. Step 8 is the final Build 3 consolidation.

At this point, we are no longer inventing anything new. We are taking Steps 1–7 and locking them into one coherent architecture so Codex later has one source of truth rather than scattered notes.

BUILD 3 — STEP 8

FINAL CROSS-LINK NORMALIZATION & MASTER DATA MODEL

The architecture should now be understood as six connected object families:

SECTION → ACTIVITY → RELATIONSHIP → GATE → STATUS → INVALIDATION

with Build 2 content sitting inside the Activity objects.

1. MASTER OBJECT MODEL

Section

Represents the 14 main systems.

Section {

id

titleEn

titleFr

order

activityIds[]

}

Example:

8 = Mechanical Services

A section is only organizational hierarchy.

It does not contain QC logic itself.

Activity

This is the main Build 2 knowledge object.

Activity {

id

sectionId

title {

en

fr

}

nodeTags[]

qualityObjective

applicability

authorityNote

requirements[]

planning[]

documentControl[]

materialControl[]

inspection {

before[]

during[]

after[]

testing[]

}

specialistBoundary

evidence[]

issues {

commonDeficiencies[]

escalationTriggers[]

}

correctiveAction[]

verification[]

closureCriteria[]

reportingAnalysis[]

qualityCheckpoint[]

watchFor[]

dontMiss[]

whyItMatters

examples[]

preConcealment {

applies

criticalChecks[]

evidence[]

relatedGateId

}

communications {

before[]

during[]

issueEscalation[]

after[]

}

outputs {

records[]

acceptanceEvidence[]

followUp[]

}

search {

aliasesEn[]

aliasesFr[]

acronyms[]

keywords[]

}

logic {

statusFamily

gateIds[]

invalidationRuleIds[]

}

}

This is where Build 2 lives.

The repeated Build 2 structure remains preserved: requirements, planning, document/material control, inspection/testing, records, issues, correction, verification, closure, reporting, and quality checkpoint.

2. RELATIONSHIPS ARE STORED OUTSIDE ACTIVITIES

This is one of the most important final decisions.

We do not write:

activity.before[]

activity.after[]

activity.interfaces[]

manually.

Instead:

Relationship {

id

sourceId

type

targetId

strength

condition

notes

}

Canonical types remain:

- REQUIRES

- INTERFACES_WITH

- GATED_BY

- TESTED_BY

- COMMISSIONED_BY

- PENETRATION_MANAGED_BY

- ACCESS_CHECKED_BY

- CLOSES_THROUGH

- AS_BUILT_FEEDS

Then the application derives:

Before
After
Interfaces
Testing
Commissioning
Closeout

automatically.

One relationship = one source of truth.

3. FINAL DIRECTIONALITY RULE

We freeze the convention permanently:

REQUIRES

Always stored:

downstream → prerequisite

Example:

2.5 REQUIRES 2.4

Never also store:

2.4 NEXT 2.5

because After is derived automatically.

INTERFACES_WITH

Stored once.

Reciprocal automatically.

8.5 INTERFACES_WITH 10.4

renders from both pages.

Other directional relationships

Always:

technical node → governing/supporting workflow

Examples:

8.9 PENETRATION_MANAGED_BY 11.7

8.6 ACCESS_CHECKED_BY 11.10

4.8 TESTED_BY 13.5

8.6 COMMISSIONED_BY 13.7

This convention never changes.

4. GATES REMAIN SEPARATE LOGIC OBJECTS

Gate {

id

name

class

purpose

inputs[]

checks[]

blockingConditions[]

releaseCondition

controls[]

invalidationTriggers[]

}

Canonical gate families remain:

- G-STR-01

- G-ENV-01

- G-ROOF-01A–E

- G-INT-01

- G-MEP-01

- G-MEP-02

- G-LS-01

- G-EXT-01

- G-EXT-02

- G-TST-01

- G-FINAL-01

No fake Section 15.

No duplicate technical content.

The gate only answers:

Can the downstream activity proceed?

5. STATUS MODELS REMAIN OBJECT-SPECIFIC

We do not create one gigantic Status enum.

Canonical families remain:

ActivityStatus

GateStatus

DeficiencyStatus

NCStatus

TestStatus

AcceptanceStatus

The common philosophy remains:

Complete ≠ Accepted
Passed ≠ Closed
Contractor says done ≠ QC verified
Accepted today may be reopened if materially changed later.

Build 2 explicitly supports this distinction in deficiency closure and test acceptance.

6. INVALIDATION REMAINS A SEPARATE RULE ENGINE

InvalidationRule {

id

trigger

affectedNodeIds[]

affectedGateIds[]

severity

actions[]

condition

}

Canonical actions:

- FLAG_FOR_REVIEW

- REOPEN_ACTIVITY

- REOPEN_GATE

- INVALIDATE_TEST

- UPDATE_RECORD_REQUIRED

This must stay separate from the normal graph because:

“These two things interact”

is not the same as:

“Changing this one can invalidate the accepted state of that one.”

7. NO DUPLICATE ISSUE WORKFLOWS

This is another major normalization rule.

We do not build independent deficiency lifecycles inside:

- concrete;

- roofing;

- mechanical;

- electrical;

- firestop;

- finishes.

Every activity contains only:

common deficiencies + escalation triggers

Actual lifecycle belongs to Section 14.

So:

Activity detects issue

↓

Section 14 common deficiency / NC workflow

↓

correction

↓

verification

↓

closure

Build 2 itself requires corrective work to restore the whole affected assembly and be verified before closure.

8. NO DUPLICATE TEST FAILURE WORKFLOWS

Similarly, individual systems define:

what gets tested

but Section 13 owns:

readiness → test → failure → correction → retest → acceptance.

We do not repeat failed-test management under each discipline.

The universal chain remains:

Test

↓

FAIL

↓

13.9 Failed-Test Management

↓

Correction

↓

13.10 Retesting

↓

PASS

↓

13.11 Acceptance Evidence

Build 2 explicitly treats acceptance evidence as the final output of the testing/commissioning system.

9. NO DUPLICATE PENETRATION WORKFLOWS

Specific technical pages remain:

- 5.6 Roof Penetrations

- 8.9 Mechanical Penetrations

- 9.9 Electrical Penetrations

- 10.3 Firestopping

But the universal interface workflow lives in:

11.7 Universal Penetrations

Therefore:

5.6 → 11.7

8.9 → 11.7

9.9 → 11.7

10.3 ↔ 11.7

The specific page explains the trade-specific checks.

The universal page explains the whole assembly.

Build 2 itself says a mechanical penetration simultaneously belongs to mechanical, structural, architectural/envelope and fire/life safety.

10. NO DUPLICATE ACCESS LOGIC

Maintainability belongs centrally to:

11.10 Access & Maintainability

Relevant activities merely point to it.

Examples:

- HVAC equipment

- BAS devices

- electrical equipment

- fire/smoke dampers

- access panels

This prevents us from rewriting the same “can someone actually service this?” logic everywhere.

11. SEARCH METADATA IS SEPARATE FROM TECHNICAL CONTENT

Build 4/6 will populate:

aliasesEn[]

aliasesFr[]

acronyms[]

keywords[]

These never affect activity IDs.

So:

reinforcement
rebar
reinforcing steel
armatures

can all resolve to:

2.2 Foundation Reinforcement

without creating four different pages.

12. LANGUAGE IS PRESENTATION, NOT ARCHITECTURE

Another final normalization rule:

The graph is language-neutral.

Internally:

activityId = 10.3

Display may be:

Firestopping

or later:

Calfeutrement coupe-feu

or:

Firestopping / Calfeutrement coupe-feu

The relationships do not care.

Therefore Build 4 will never duplicate the graph.

13. NODE TAGS ARE METADATA, NOT RELATIONSHIPS

We freeze this.

Tags such as:

- preConcealment

- highControl

- traceabilityCritical

- specialistInterface

- testing

- commissioning

- interface

- closeout

are attributes.

They enable filtering and presentation.

Example:

Show all pre-concealment activities

can filter nodeTags.

No need for 80 PRE_CONCEALMENT relationships.

14. CONDITION VOCABULARY

We should freeze the controlled conditions too.

Canonical conditions:

always

whereApplicable

whereSpecified

whereRated

whereFireSeparation

whereExterior

whereExteriorEnvelope

whereRoof

whereConcealed

whereTestingRequired

whereEquipmentPresent

whereSystemPresent

whereBuried

whereSpecialistRequired

We can add a condition later only if genuinely necessary.

No free-text conditions everywhere.

15. STRENGTH VOCABULARY

Canonical relationship strength:

hard

conditional

coordination

Nothing else.

hard

Normally required.

conditional

Required only when stated condition exists.

coordination

Must be considered but not inherently blocking.

This keeps the graph understandable.

16. SPECIALIZED NODE FAMILIES

We now formally define four page-template families.

standardActivity

Most of Sections 1–10 and 12.

Uses full common Activity schema.

interfaceActivity

Especially Section 11 and nodes like:

- 8.9

- 9.9

- 10.4

Emphasizes:

- systems involved;

- sequence;

- compatibility;

- restoration;

- access;

- evidence.

testingActivity

Section 13.

Emphasizes:

- readiness;

- procedure;

- instruments;

- personnel;

- result;

- failed-test management;

- retest;

- acceptance evidence.

closeoutActivity

Section 14.

Emphasizes:

- open items;

- assignment;

- correction;

- verification;

- evidence;

- acceptance;

- records.

Gate pages remain their own logic page:

gatePage

17. SECTION ROLE NORMALIZATION

The 14 sections are now not all conceptually equal.

We can classify them:

Construction / physical systems

1–10, 12

Interface intelligence

11

Verification / performance

13

Completion / evidence / turnover

14

This classification helps homepage/navigation design later.

It does not change the numbering.

18. THE FINAL GLOBAL GRAPH

Conceptually, the whole application now looks like this:

┌─────────────────────┐

│  BUILD 2 KNOWLEDGE  │

│   Activities 1–14   │

└─────────┬───────────┘

│

Relationships

│

┌──────────────────┼──────────────────┐

│                  │                  │

BEFORE            INTERFACES          AFTER

│                  │                  │

└──────────────┬───┴──────────────────┘

│

GATES

│

Can work proceed?

│

┌────────────┴────────────┐

│                         │

YES                       NO

│                         │

downstream work           Issue / NC

│                         │

│                   Correction

│                         │

│                   Verification

│                         │

└──────────────┬──────────┘

│

TESTING

│

┌──────┴──────┐

│             │

PASS          FAIL

│             │

│        Correct/Retest

│             │

└──────┬──────┘

│

Acceptance Evidence

│

Closeout

│

Turnover

And at any point:

Later modification

↓

Invalidation rule

↓

Affected activity/gate/test re-reviewed

That is our complete Build 3 architecture.

19. FIELD PAGE DATA FLOW

When the user opens:

8.9 Mechanical Penetrations

the application does this:

1. Fetch Activity 8.9

Gets Build 2 technical content.

2. Query relationship registry

Gets:

- prerequisites;

- interfaces;

- universal penetration workflow;

- testing;

- downstream work.

3. Query gate registry

Gets:

- G-MEP-01;

- G-INT-01 where applicable;

- G-ENV-01 where exterior;

- etc.

4. Query invalidation rules

Gets:

- new penetration;

- opening modification;

- disturbed firestop;

- envelope restoration changes.

5. Apply conditions

Rated?

Exterior?

Roof?

Concealed?

6. Build UI

Quick / Full / Learn comes later in Build 5.

This means we never write a page manually.

The app assembles it from structured data.

20. CROSS-LINK DEDUPLICATION RULE

If the same destination is discovered through several routes:

Example:

8.9 Mechanical Penetrations

directly interfaces with 10.3 Firestopping

and also reaches it through 11.7 Universal Penetrations.

The UI should prioritize:

Direct relationship

and not show duplicate indirect links.

Priority:

- direct hard relationship;

- direct conditional;

- direct coordination;

- hub/indirect discovery.

21. CONDITION RESOLUTION RULE

Suppose an activity has:

8.9 INTERFACES_WITH 10.3

condition = whereFireSeparation

The universal guide does not know your actual wall type.

So the UI should show:

Firestopping — if penetrating a fire-rated assembly

It does not automatically assume the condition is true.

This is central to keeping the guide universal.

22. AUTHORITY RULE

At the architecture level:

The application may guide what to verify, but it never invents project acceptance authority.

Every specialist-sensitive node can carry:

specialistBoundary.required = true

and show:

Verify applicable PIE/PRIE / governing project procedure and coordinate with authorized specialist.

This is particularly important in electrical, fire alarm, NDT, commissioning and technical dispositions.

23. PROJECT-SPECIFIC DATA IS EXCLUDED

We formally freeze this as an out-of-scope rule for the MVP.

No:

- CRT procedures;

- Hochelaga drawings;

- actual PIE numbers;

- project personnel;

- live deficiencies;

- live NCR register;

- live test register;

- actual inspection signatures;

- project database.

Our system is:

Universal QC guidance architecture

not:

parallel project QMS.

That boundary remains deliberate.

24. BUILD 3 QUALITY-CONTROL CHECK

Before we declare Build 3 finished, verify the architecture against our own criteria.

Can every technical activity be uniquely identified?

Yes.

Can every page know where it belongs?

Yes — sectionId.

Can it know what comes before?

Yes — REQUIRES.

What comes after?

Yes — reverse REQUIRES.

What touches it?

Yes — INTERFACES_WITH.

What gate controls it?

Yes — GATED_BY.

What test applies?

Yes — TESTED_BY.

What commissioning applies?

Yes — COMMISSIONED_BY.

Can penetrations share a universal workflow?

Yes — 11.7.

Can maintainability be cross-checked?

Yes — 11.10.

Can deficiencies use one lifecycle?

Yes — Section 14.

Can test failures use one lifecycle?

Yes — Section 13.

Can accepted work later be reopened?

Yes — Invalidation Registry.

Can conditions remain universal?

Yes — controlled condition vocabulary.

Can the interface later become bilingual?

Yes — language-neutral IDs.

Can Quick/Full/Learn reuse the same content?

Yes — common Activity schema.

Can search aliases be added without changing technical content?

Yes.

Can this be implemented without duplicating dozens of links?

Yes.

So the architecture passes.

25. FINAL BUILD 3 DATA PACKAGE

Codex will eventually need approximately these datasets:

sections

activities

relationships

gates

invalidationRules

statusModels

conditionDefinitions

nodeTagDefinitions

Later Build 4 adds:

translations

searchAliases

acronyms

Build 5 adds/polishes:

watchFor

dontMiss

whyItMatters

quickPresentation

learnPresentation

compositeWorkflows

Build 6 deals mainly with UI behavior and usability.

That dependency order is clean.

26. BUILD 3 — ARCHITECTURALLY FROZEN

We can now officially lock:

Canonical Section Registry ✓

Canonical Activity Registry ✓

Canonical IDs ✓

Canonical Node Tags ✓

Relationship Registry ✓

Directionality Rules ✓

Reciprocity Rules ✓

Conditions ✓

Strength Levels ✓

Gate Registry ✓

Gate Status Model ✓

Global Status Families ✓

Invalidation Registry ✓

Controlled Propagation ✓

Common Activity Schema ✓

Specialized Page Families ✓

Navigation Derivation ✓

No duplicate issue lifecycle ✓

No duplicate failed-test lifecycle ✓

No duplicate penetration workflow ✓

No duplicate access workflow ✓

Language-neutral architecture ✓

Project-QMS boundary ✓

BUILD 3 COMPLETE.

And this is genuinely a good stopping point. We should not continue tweaking Build 3 now unless Build 5 exposes an actual usability problem.

The next work should be Build 5 — defining exactly how QUICK / FULL / LEARN behave, because that is the layer that turns this very sophisticated backend architecture into something you can actually use quickly on a tablet without seeing all of this complexity.